SANITATION SAFETY PLANNING

IN JA-ELA/EKALA AREA

Prepared By:

Regional Manager - Water Reclamation

Ja-Ela/ Ekala Office

National Water Supply and Drainage Board

January 2025

TABLE OF CONTENTS

INTRODUCTION	8

1.	PREPARATION FOR SANITATION SAFETY PLAN (SSP)	10

1.1 The SSP Area and the Lead Organization	10

1.2 The SSP Team	10

1.3 Establishment of SSP Priorities	20

2.	SYSTEM DESCRIPTION	23

2.1 System Map	23

2.2 Characterize System Flows	35

2.3 Identify Exposure Groups	39

2.4 Supporting Information	47

3. HAZARDOUS EVENTS, ASSESSMENT OF EXISTING CONTROL MEASURES AND RISK EXPOSURE	48

3.1 Identification of Hazards and Hazardous Events	48

3.2 Identification and Assessment of Existing Control Measures	50

3.3 Assessment and Prioritization of Risk Exposure	59

4.	DEVELOPMENT AND IMPLEMENTATION OF INCREMENTAL IMPROVEMENT PLAN	60

4.1 Consideration of Options to Control Identified Risks	60

4.3 Implementation of the Improvement Plan	67

5.	MONITORING OF CONTROL MEASURES AND VERIFICATION OF PERFORMANCE	68

5.1 Definition and Implementation of Operational Monitoring	68

5.2 Verification of System Performance	80

5.3 Auditing the System	80

6.	DEVELOPMENT OF SUPPORTING PROGRAMMES AND REVIEW PLANS	81

6.1 Identification and Implementation of Supporting Programmes	81

6.2 Periodic Reviewing and Updating the SSP Outputs	82

LIST OF TABLES

Table 2: The Operation Team	12

Table 3: The Stakeholder Team	13

Table 4: Stakeholder Analysis	16

Table 5: Characterization of System Flow	36

Table 6: Exposure Groups	40

Table 7: Characterization of Exposure Groups	42

Table 8: Supporting Information	47

Table 9: Risk Definitions for Semi-quantitative risk assessment	48

Table 10: Semi-Quantitative Risk Assessment Matrix	49

Table 11: Risk Assessment	51

Table 12: Priorities Hazardous Event with High Risk	59

Table 13: Control Option for Conveyance of Sewer through the Network and Pumping Station	60

Table 14: Control Option for Conveyance of Sewer through the Network and Pumping Stations	61

Table 15: Control Option for Septic sump and Sludge tank cleaning	61

Table 16: Control Option for Disposal of Dried Sludge	62

Table 17: Control Option for Disposal of Dried Screen	63

Table 18: Climate Adaptation for a Specific Sanitation Step	64

Table 19: Improvement Plan	65

Table 20: Operational Monitoring Overview	68

Table 21: Operational Monitoring Plan for P1; Toilet and IC of house, commercial, and industrial establishment	70

Table 22: Operational Monitoring Plan for T1; Conveyance of Sewer through the network and Pumping Stations	71

Table 23: Operational Monitoring Plan for T1; Conveyance of Sewer through the network and pumping station	71

Table 24: Operation Monitoring Plan for T1; Conveyance of Sewer through the network and pumping station.	72

Table 25: Operational Monitoring Plan for T1; Conveyance of Sewer through the network and pumping stations.	72

Table 26: Operational Monitoring Plan for T1; Conveyance of Sewer through the network and pumping station.	73

Table 27: Operational Monitoring Plan for T1; Conveyance of Sewer through the network and pumping stations	73

Table 28: Operational Monitoring Plan for T1; Conveyance of FS by Vacuum Truck	73

Table 29: Operational Monitoring Plan for T1; Conveyance of FS by Vacuum Truck	74

Table 30: Operational Monitoring Plan for T1; Conveyance of FS by Vacuum Truck	75

Table 31: Operational Monitoring Plan for P4; Treatment Process at Ekala WRC	75

Table 34: Operational Monitoring Plan for P4; Treatment Process at Ekala WRC	77

Table 35: Operational Monitoring Plan for P4; Treatment Process at Ekala WRC	77

Table 36: Operational Monitoring Plan for P4; Treatment Process at Ekala WRC	78

Table 37: Operational Monitoring Plan for P4; Treatment Process at Ekala WRC	78

LIST OF FIGURES

Figure 1: Ekala Water Reclamation Centre	8

Figure 2: System Map	25

Figure 3: Flow Diagram	33

Figure 4: System Flow Diagram	35

Figure 5: Exposure Group	41

Abbreviation

| BOD | Biochemical Oxygen Demand |
| --- | --- |
| CEA | Central Environmental Authority |
| CMR | Compliance Monitoring Report |
| COD | Chemical Oxygen Demand |
| DA | Department of Agriculture |
| FOG | Fat, Oil, and Grease |
| LA | Local Authority |
| MOH | Ministry of Health |
| NWSDB/ NWS&DB | National Water Supply and Drainage Board |
| PHI | Public Health Instructor |
| PPE | Personal Protection Equipment |
| PS | Pump Station |
| RSC | Regional Support Center |
| SSP | Sanitation Safety Plan |
| SSC | Sewer Service Connection |
| STP | Sewage Treatment Plant |
| TP | Treatment Plant |
| TSS | Total Suspended Solids |
| UDA | Urban Development Authority |
| VT | Vacuum Truck |
| VTU | Vacuum Truck Unit |
| WR | Water Reclamation |
| WWTP | Wastewater Treatment Plant |
| WWTS | Wastewater Treatment System |

Definition of Terms

Bio solids – Organic materials resulting from the treatment of sewage and septage sludge; residue generated during the treatment of domestic sewage and septage in a treatment facility

NWS&DB – National Water Supply and Drainage Board

Desludging — The process of cleaning or removing the accumulated domestic sludge or septage.

Dewatering — This is the process of reducing the moisture content of sludge to lessen the volume and odor, e.g. vacuum, filter, centrifuge, belt filter press, filter press, sludge drying beds, and lagoons.

Disinfection — This is the process of destroying pathogenic organisms either by physical (e.g. application of heat) or chemical (e.g. chlorine application) means.

Effluent – A general term denoting any wastewater, partially or completely treated, or in its natural state, flowing out of a manufacturing plant, industrial plant, or treatment plant.

Exposure— Contact of a chemical, physical or biological agent with the outer boundary of an organism (e.g. through inhalation, ingestion, or dermal [skin] contact).

Hazard—A biological, chemical, or physical constituent that can cause harm to human health Helminth— Helminths are a broad range of organisms that include intestinal parasitic worms: trematodes (flatworms, also commonly known as flukes, e.g. Schistosoma), nematodes (roundworms, e.g. Ascaris, Trichuris and the human hookworms) or Cestodes (tapeworms, e.g. Taenia solium, the "pork tapeworm")

Influent – Waste water flowing through the sewer lines/conveyance into a treatment plant

Pathogens – Disease-causing organisms (e.g. bacteria, helminths, protozoa, or viruses).

Risk – The likelihood and consequences that something with a negative impact will occur.

Septage - Also known as Domestic Sludge or the solid particle of domestic sewage, which settles at the bottom of the sedimentation tank and is digested by anaerobic bacteria, purely from domestic sources, exclusive of industrial and hazardous wastes.

Sewage - or also known as Domestic Sewage — wastewater composed of raw liquid and solid waste coming from residential and commercial uses, exclusive of industrial and hazardous waste.

Wastewater – Sewage and faecal sludge

# INTRODUCTION

### Due to the increasing challenges posed by human diseases stemming from the inadequate or improper use of sanitation facilities, communities must establish systems to address these challenges and mitigate their effects. In addition to the adequacy of sanitation facilities, issues such as inadequate containment, improper treatment, and poor handling of excreta and wastewater must also be addressed, as they contribute to the problem. The National Water Supply and Drainage Board (NWS&DB) has initiated the development of a Sanitation Safety Plan (SSP) to cover the entire country. As part of this initiative, the Ja-Ela/Ekala Sanitation Safety Plan has been developed to ensure the safety of personnel involved in sanitation activities in the Ja-Ela, Mahara, Wattala, Dompe, and Gampaha DS divisions in the near future.

Ekala Water Reclamation System

The coverage area includes the part of Ekala which covered by the Ekala sewer network area including Niwasipura, Milanium City, Ekala Air force Camp, IDB. This SSP was created for the wastewater management system mentioned above.

Figure 1: Ekala Water Reclamation Centre

The Ekala Water Reclamation Center (WRC) is a combined sewage and faecal sludge treatment facility that receives sewage from the sewered areas of Ja-Ela/Ekala and faecal sludge from the surrounding sewered and unsewered areas. A total of 687 utilities, including the bulk meter connection of Millennium City (which has 820 units) and the bulk meter connection of Nivasipura (which has 1,200 units), are already connected to the sewers of the Ja-Ela/Ekala sewerage system. More than 15,000 residents and 1,000 floating population members benefit from the system.

The sewage is conveyed to the water reclamation center through a network that includes 3 lifting stations and 226 manholes, spanning 26 km of sewers. The following figures show the water reclamation center and the coverage area served by the sewer network associated with the treatment plant. With this SSP, NWS&DB aims to identify all potential hazards and quantify the risk associated with exposure to the sewage and faecal sludge throughout the sanitation chain including exposure to the end-products produced by the treatment facilities, particularly the effluent and the dried bio-solid

# PREPARATION FOR SANITATION SAFETY PLAN (SSP)

## 1.1 The SSP Area and the Lead Organization

SSP area

The area of the system includes of the entire wastewater infrastructure managed by the NWSDB. It is included household connections in the Ja-Ela/Ekala area, Millennium City housing scheme, Nivasipura housing scheme, Ekala Air force camp sewer network, pumping stations, water reclamation center (WRC), treatment and disposal of sludge,  reuse and disposal of treated effluent. Since, some houses are served with on-site systems (e.g. Septic tanks and soakage arrangements), the faecal sludge management system, where workers, users, and community are exposed to wastewater (Sewage and faecal sludge) during collection, transport, treatment and disposal, is also included.  Fecal sludge treatment covers the Ja-Ela, Mahara, Wattala, Dompe, and Gampaha DS divisions.

Lead organization

National Water Supply and Drainage Board (NWSDB) is the SSP lead organization.

## 1.2 The SSP Team

SSP team leader

The Regional manager-Jaela/Ekala, water reclamation division of NWSDB has been appointed as the SSP team leader, with many years of experience in developing sanitation projects. They possess the resources, knowledge and management skills to lead project implementation.

Table 1: SSP Supportive Team

|  | Name | Job Title | Role | Responsibility | Contact No |
| --- | --- | --- | --- | --- | --- |
| 01 | Eng. Dhanesh Gunathilake | Additional General Manager – Water reclamation (NWSDB) | Facilitator | Assist to implement SSP by allocating financial and Human resources. Reporting the progress to the top management. Monitoring the functionality of the SSP and coordinate with top management of relevant Stakeholder organizations. | 0773856724 |
| 02 | Eng. G.D.N. Neville | Deputy General Manager – (WR) (NWSDB) | Facilitator | Assist to implement SSP by allocating financial and Human resources. Reporting the progress to the top management. Monitoring the functionality of the SSP and coordinate with top management of relevant Stakeholder organizations. | 0772918634 |
| 03 | Eng. Jayawardana | Water Reclamation Specialist (NWSDB) | Member | Guidance on water quality issues, and wastewater treatment. Advise to provide new improvements. | 0764503487 |
| 04 | Eng. S.N. Fernando | Assistant General Manager - GCWR (NWSDB) | Facilitator | Monitoring the functionality of the SSP and coordinate with top management of relevant Stakeholder organizations. | 0772386182 |
| 05 | Eng. K. Kuruppu | Assistant General Manager WR (NWSDB) | Facilitator | Monitoring the functionality of the SSP and coordinate with top management of relevant Stakeholder organizations. | 0773440686 |

Table 1: The Operation Team

| NAME/JOB | Section | TITLE | Expertise | ROLE IN SSP TEAM | CONTACT INFORMATION |
| --- | --- | --- | --- | --- | --- |
| W.C.A Gunaratne | WR ( Ja Ela/Ekala Region) | Regional Manager | Charted Engineer (Civil) | Team Leader | 0772240577 |
| D.M.W.J.B.Dissanayake | WR ( Ja Ela/Ekala Region) | Engineer (Civil) | Engineer (Civil) | Facilitator | 0764583668 |
| Eshani Jayathilake | Laboratory (Soysapura WRC) | Chemist (Moratuwa/Rathmalana) | Water Quality | Water quality testing | 0771453791 |
| W. Athulathmudali | GCWR | Accountant (GCWR) | Financial | Financial Facilitator | 0718066289 |
| Amali Jayakodi | WR Section | Sociologist | SSP Moderator | Conducting meetings and awareness programs | 0715220242 |
| D.W Suresh Ranjith Lal | Ekala WRC | OIC (EWRC) | Civil Engineering | Deputy Team Leader, Health and Safety officer, O&M of WRC & coordination. | 707517860 |
| S.S.A. Madubhasa | O&M | EA (Civil) | Civil Engineering | O&M of WRC & coordination. | 0711141848 |
| G.R.D.M.Iddamalgoda | WR ( Ja Ela/Ekala Region) | EA(Mech.) | Mechanical Engineering | O&M of mechanical section | 0716407880 |
| H.L.P.K.Gunawardana | O&M | EA (Electrical) | Electrical Engineering | O&M of electrical section | 0773900557 |
| H.D.M.Perera | O&M | EA (Civil) | Civil Engineering | O&M of documentation & procurement. | 0763570891 |
| U.G. K. Perera | O&M | Lab Ass: | Sample testing | Process monitoring | 0706587888 |
| M.S. Jummar | O&M | Plant Technician | Pump Operation | Plant operation | 0717760192 |
| W.S. Sahan kumara | O&M | Plant Technician | Pump Operation | Plant operation | 0718899743 |
| Chamil Asanka | O&M | Plant Technician (Covering) | Pump Operation | Plant operation | 0776315005 |
| P.A Somarathna | O&M | Mechanic | Mechanical works | O&M of mechanical section | 0715378944 |
| D.T.M.H. Kumara | O&M | Driver | Driving | Driving vehicles | 0713478545 |
| P.A.D. Priyantha | O&M | Driver | Driving | Driving vehicles | 0707857556 |
| W.W.N. Annesly | O&M | Labour | Documentation and store keeping | Maintenance of necessary stocks | 0716233559 |
| M.M.P.S.S. Fernando | O&M | Labour | O&M work | Assisting for Maintenance Work | 0716233559 |
| W.S.K. Fernando | O&M | Labour | O&M work | Assisting for Maintenance Work | 0743059833 |
| E.A.S.T.Senadeera | O&M | Labour | O&M work | Assisting for Maintenance Work | 0741021015 |
| A.V.C. Dilshan | O&M | Labour | O&M work | Assisting for Maintenance Work | 0788627269 |
| S.A.A.U. Perera | O&M | Labour | O&M work | Assisting for Maintenance Work | 0759519305 |

Table 2: The Stakeholder Team

| SANITATION STEP | SSP TEAM MEMBERS AND REPRESENTATION | CONTACT INFORMATION |
| --- | --- | --- |
| Toilet and Containment – (Storage/treatment) | Secretary - Gampaha Urban Council Secretary - Ja-Ela Pradeshiya sabha Secretary – Mahara Pradeshiya sabha Secretary – Dompe Pradeshiya sabha Secretary – Gampaha Pradeshiya sabha Secretary – Waththala Pradeshiya sabha | 0332223392 0112236306 0112927076 0332267475 0332222020 0114329352 |
|  | Director - Central Environmental Authority Gampaha branch | 0703097850/ 0112872359 |
|  | OIC Environmental – Gampaha Police station OIC Environmental – Ja-Ela Police station OIC Environmental – Kadawatha Police station (for Mahara) OIC Environmental – Dompe Police station OIC Environmental – Waththala Police station | 0332222222 0112236222 0112925222 0112409222 0112930222 |
|  | Gampaha Divisional Secretory – Gampaha Divisional Secretariat Dompe Divisional Secretory – Dompe Divisional Secretariat Waththala Divisional Secretory – Waththala Divisional Secretariat Mahara Divisional Secretory – Mahara Divisional Secretariat Ja-Ela Divisional Secretory – Ja-Ela Divisional Secretariat | 0766520823/ 0717178698 0332267167 0112930384 0112970769/ 0112970713 0112236126/ 0112247797 |
|  | Seeduwa Medical officer of health – Seeduwa(MOH) officer | 0112252660 |
|  | Public health investigator (PHI) – Gampaha(MOH) office Public health investigator (PHI) – Dompe(MOH) office Public health investigator (PHI) – Waththala(MOH) office Public health investigator (PHI) – Mahara(MOH) office Public health investigator (PHI) – Ja-Ela(MOH) office | 0332222278 0112404769 0112933212 0112973506 0112237525 |
|  | Chairman - Welfare Organizations in Nivasipura Housing Scheme Chairman - Welfare Organizations in Millennium City Housing Scheme | 0112292934 0742020177/ 0742020178 |
| Conveyance (Emptying and transport of sewage and/or faecal sludge) | SSP team leader – NWSDB O&M Engineer – NWSDB OIC (Ekala-WRC) – NWSDB OIC (CN – EWRC) - NWSDB EA (Civil) (Ekala-WRC) – NWSDB EA (Mec) (Manager office) – NWSDB EA (Electrical) (Ekala WRC) – NWSDB Area Engineer – CEB JaEla Area Engineer – SLT JaEla Fecal Sludge supplier - Amashan - Anoma Construction - Araliya Cleaners. - Ceylon Grain Elevators PLC - Chaminda Enterprises - Dompe pradesiya saba - Eco bowser Service - Eco Clean service - Flexi print - Gampaha MC 12. Gampaha Pradesiya Sabha 13. J.A Palitha Jayasinhe. 14. Ja - Ela pradesiya saba 15. Kent silvering Cleaners 16. Madunadee inter Pvt Ltd 17. Mahara Pradeshiya Sabha 18. Mahara Prison 19. Mahela Cleaners 20. Minuwangoda MC 21. Police station Pamunugama 22. Pulina Induwara Enterprises Pvt Ltd 23. Seeduwa Katunayake MC 24. Sethma Hospital - Gampaha 25. St Anthoni's Service 26. Super clining services Lanka Ltd. 27. T.D Lakmal 28. Texlan Center Pvt Ltd. 29. Thimira Enterprises Pvt Ltd 31. Waththala PS 32. Sakura Auto Engineers 33. Hedala Clean Services 34. Jaya Sri Environmental Services 35. AB Hydrotech 36. Limo Logistics 37. R V S Thushara Sampath 38. J & W Brothers 39. Tharidu Washing Pvt Ltd 40. Palith & Company 42. Veyangoda Bowser service 43. Eco Septic Services 44. D W Transport Services 46. DP Waste Management | 0772240577 0764583668 0707517860 0761267045 0711141848 0716407880 0773900557 0112232105 0112245795 0774177034 0774227693 0775168128 0112497000 0776224245 0705269260 0777307072 0710115577 0112973797 0332230808 0710623157 0723046189 0112236306 0714335459 0777209450 0756561305 0114677545 0718792886 0112295275 0112236340 0761418213 0112253575 0334626626 0773140544 0112231668 0714595716 0112295652 0775885008 0112958492 0777953072 0777310821 0773350350 0117717777 0760247777 0771226896 0711900300 0779743753 0718366579 0702890700 0777307072 0778850850 0772302302 |
|  | Private and Public (NWSDB and pradeshiya sabha) vacuum truck operators, Sanitation workers and service providers |  |
| Treatment and disposal | SSP team leader, O&M Engineer, OIC (Ekala-WRC), EA (Civil), EA (M&E), EA (Electrical), Lab Assistant, Plant technicians, Irrigation Department, Central Environmental Authority. |  |
|  | Katana Area Officer - Central Environmental Authority (CEA) JaEla Area Officer - Central Environmental Authority (CEA) | 0332232201 033223201 |
| Reuse | Water reclamation center (WRC- Ekala) | 0112289052 |
|  | Irrigation department | 0112581162 |
|  | Department of agriculture | 0112092667 |

Stakeholder analysis

Because of the size and complexity of the sanitation systems in Ekala, the SSP core team has decided to conduct a stakeholder analysis to ensure that all relevant stakeholders were engaged. After a brainstorming session, a list of stakeholders representing the entire sanitation service chain identified and analyzed.

Table 3: Stakeholder Analysis

| Sanitation step | Stake holder | Role of stake holder | Motivating factors | Constraining Factors | Importance | Influence/Power | Partition Require |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Entire Sanitation chain | NWSDB | Direct control and oversight of implementation of national guidelines and Standards at each step of the chain. | SSP will help to identify the right sanitation interventions. | Too much effort and insufficient resources | High | High | Empowerment |
| Entire Sanitation chain | District/ Divisional Secretariat | Influence–coordinate with other government organization to ensure | Providing safe sanitation services is a requirement for Healthy communities. | Low knowledge about their role in the sanitation sector. | Low | High | Collaboration |
|  |  | that sanitation systems |  |  |  |  |  |
|  |  | do not pose public |  |  |  |  |  |
|  |  | Health risks. |  |  |  |  |  |
| Entire sanitation chain | Public health official MOH, PHI | Ensuring the public health and providing awareness about the sanitation. | They have been developing studies on water borne diseases. | The scope of their job role is wider. As a result, they have limited time to involve in sanitation sector. | High | Low | Consultation |
| Entire sanitation chain | Secretary of Local authority (PS, UC,MC) | Direct control–Support from the legislative branch of the local Government. | They have the legislative power to address the sanitation safety within their boundaries | Lack of experience and interest in sanitation. | High | High | Collaboration |

| Sanitation step | Stake holder | Role of stake holder | Motivating factors | Constraint Factors | Importance | Influence/ Power | Participation Requirement |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Entire sanitation chain | Chairman of PS | Allocation of funds from local government. | Commitment to the government to improve their cities in every aspect. | Allocation of lesser funds for sanitation improvements and preferring government funds to be allocated to other sectors. | Low | High | Collaboration |
| Entire sanitation chain | Waste and wastewater service workers | Influence –representatives of formal and informal sanitation workers advocating for fair working conditions and pay. | Workers along the chain will be responsible for Implementing proposed system improvements and monitoring, and can evaluate the practicality and safety for Workers in the system. | Limited representation of workers | High | Medium | Collaboration |

| Sanitation step | Stake holder | Role of stake holder | Motivating factors | Constraining Factors | Importance | Influence/Power | Partition Require |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Sewered system (flush toilet with sewerage and off-site wastewater treatment) |  |  |  |  |  |  |  |
| Toilet | Residents of Ekala/Jaela. | Functioning the waste water system in their premises correctly. |  |  | High | Low | Collaboration |
| Conveyance and treatment and disposal | O&M Ekala Team, WRC | Operate and maintain the wastewater conveyance, treatment and disposal system. | Lead organization in sanitation safety plan implementation. | Rising the cost of spare parts. | High | High | Information |
| Conveyance | RDA/PRDA | Approving and providing estimates for road damages due to excavations for leak repairs and new connections. Reinstatement of roads. |  | Resistance to approve the road damages. | High | High | Collaboration |
| End-use/ disposal | CEA | Enforcing laws and regulations related to treated effluent discharge and sludge disposal | Possible improvements to sludge management process. | Resources and capacities to monitor dried sludge quality are lacked. | High | High | Collaboration |
| End use | Department of Agriculture | Develop official guidelines and quality standards for agricultural products, and conduct training and projects with farmers. | Use of treated wastewater and dried sludge for, agricultural purposes. | Resources and staff are lacked. | High | Low | Collaboration |

| Sanitation step | Stake holder | Role of stake holder | Motivating factors | constrain Factors | Importance | Influence / Power | Participation Required |
| --- | --- | --- | --- | --- | --- | --- | --- |
| End use | Farmers | Use treated wastewater which is discharged to the Dandugam Oya | Using dried sludge for cultivations as a fertilizer | Less of knowledge on sanitation | High | Low | Consultation |
| On-site system (flush toilets with septic tanks and effluent infiltration, and off-site faecal sludge disposal) |  |  |  |  |  |  |  |
| Toilet, containment –storage/treatment | House Owners Local Authority | In charge of maintaining their own on-site systems and should cover the costs of refurbishment and upgrading. | They would be interested in increasing property values. | They are concerned about the costs of repairing and refurbishing their on-site system. | Low | Low | Collaboration |
| Conveyance | Vacuum tanker operators –private and public providers | Emptying cesspools and septic tanks | They are motivated by legalization and recognition | Lack of competent workers. Some discharging points are far away from their collection sites. Increase in the transportation cost | High | High | Consultation |
| Disposal | CEA | Have a surveillance team that monitors illegal waste discharges to the environment. However, they have not given enough focus on vacuum Tankers | SSP supports their overall aim of providing leadership in environmental protection | This could represent new tasks that have not been included in strategic planning | High | High | Empower |

Establishment of steering committee

Following the results of the stakeholder analysis, the SSP core team has decided to invite the following people to form the SSP steering committee:

- District Secretariat – Gampaha

- Head of Water Reclamation Section of NWSDB

- Members of Local Authorities (MCs/UCs/PSs) – Mayor/Chairman/Secretary (Ja- Ela/Gampaha /Seeduwa)

- Divisional Secretaries– Ja-Ela/Dompe/Mahara/Watthala/Gampaha DS divisions

- Head of CEA – Gampaha

- Head of UDA – Gampaha

- Head of Regional Health Department (MOH) – Gampaha

- Head of Agricultural Department - Gampaha

- SSP Team Leader in NWSDB

## 1.3 Establishment of SSP Priorities

Due to limited resources, it was not feasible to develop SSP for all sanitation systems in Ja-Ela/Dompe/Mahara/Watthala/Gampaha and other areas. The SSP core team has hosted a kick-off meeting with members of the SSP steering committee. The main objective of the meeting is to decide which sanitation systems should be prioritized by SSP and which target systems are likely to pose the greatest health risks.

Excreta flow diagrams (SFDs) are a simple and effective way of visualizing the service types in a city and the fate of different excreta streams. Green arrows represent the proportions of excreta that are “safely managed” along the sanitation chain. Red arrows show where the excreta flows are not safely managed.

Members of the steering committee have decided to consider following priority areas in SSP;

- Sewered Areas in Ja-Ela/Ekala WRC

- Unsewered Areas – Serviced by Faecal Sludge Management (Those who are having only onsite sanitation facilities)

Sewered areas

Given the extensive network of Ja-Ela/Ekala sewers, there are still households in the area that are not connected to the system. Households with septic tanks are provided with faecal sludge management services through NWSDB or third party vacuum trucks, especially when tapping them to the existing sewers is not feasible (i.e., due to location of households relative to sewers and due to cost concerns).

There are also instances, interception chambers from households connected to the sewers or manholes overflow due to blockages. A sewerage system which is properly operating and maintaining can capture domestic wastewater from sources and direct it to a wastewater treatment facility. Eventually, treated effluent is reused, and excess discharges to a water body according to CEA discharge standards.

Unsewered areas

In the unsewered areas within and outside the limits of the wastewater treatment plants of Ja-Ela/Ekala, sewage is handled by onsite sanitation systems such as septic tanks and soakage pits. Houses with septic tanks and soakage arrangements located in these areas are regularly served by Ja-Ela/Ekala water reclamation center through NWSDB own vacuum trucks (Ja-Ela/Ekala - 01) or third party vacuum trucks (Such as those operated by pradeshiya sabha, urban council, municipal council or private party).

Ja-Ela/Ekala area ground water table is considerably higher and type of soil in most of the areas is having lower percolation rate. Hence, it is not ideal to use unlined septic tanks or soakage arrangements (Soakage pits or trenches).Although the current situation is having a mix of lined and unlined septic tanks with soakage arrangements. Water reclamation centers utilize vacuum truck units (VTUs) to collect faecal sludge from customers in unsewered areas. The VTUs have to service selected areas each day to ensure septic tanks of all customers are emptied once in every 3 - 5 years.

There are also instances, when customers request immediate desludging (e.g., overflowing septic tanks) which are classified as unplanned activities, water reclamation centers will cater to such requests having spare capacity. Such desludging requests are 	handled by either NWSDB or third party vacuum trucks.

Customers have to support the desludging activities. Once, VTUs have reached the premises which requires desludging, the personnel prepare the hose to be used, opens the septic tank cover slab or manhole cover and proceed the desludging work. After desludging work is finished, VTU personnel will cover the septic tank and customer has to seal it. Then the VTU and personnel will move on to another desludging work 	until the VTU reaches to its maximum capacity. Finally, the VTU will depart to the wastewater treatment facility.

# SYSTEM DESCRIPTION

The regional manager of the water reclamation section of Ja-Ela/Ekala of NWS&DB handles the provision of sewer service connections, maintenance and repair of the sewer network, handling of customer complaints, operation and maintenance of the wastewater facilities (Sewage and faecal sludge), and planning for sewerage coverage expansion. For the sanitation services, its main tasks are included the provision of regular cleaning services of septic tanks, sewage and faecal sludge management, handling customer complaints, fleet maintenance, and planning for sanitation coverage expansion in Ja-Ela/Ekala water reclamation system.

Sewered areas are provided with sewerage services that include the installation of new sewer service connections, operation, and maintenance of sewage treatment facilities (Ja-Ela/Ekala), conveyance systems, and the sewer network. Areas that cannot be connected to the sewers, but have septic tanks, are provided with faecal sludge management services .These services include desludging and treatment of septic tank wastewater on request, as well as coordination works with the customers.

## 2.1 System Map

Ja-Ela/Ekala water reclamation system

The system starts with households where wastewater is generated (Domestic wastewater). Households are either connected to the sewer line or serviced by VTUs to enable the transport of the faecal sludge to the treatment plant. In addition to households, wastewater from commercial customers is accommodated as long as their wastewater is domestic in nature and industrial wastewater after pre-treatment. This is verified through field investigations of the commercial and industrial establishments. In areas where sewers are available, commercial establishments can be connected to the nearest sewer and are required to have oil and grease trap to prevent oil and grease to discharge to the sewer lines.

The water reclamation system of Ja-Ela/Ekala is included with a municipal wastewater treatment facility (Ja-Ela/Ekala WRC) and Ja-Ela/Ekala WRC is a combination of preliminary treatment, secondary treatment, and disinfection. Wastewater is accepted by the WRC for treatment safely disposal to comply with the National Environmental standards. The wastewater treatment plant at the center is compromised uses a variety of techniques and technologies to remove pollutants from the influent wastewater. These techniques and technologies are included physical, chemical, and biological processes.

The WRC is located on a 6 acre land lot at Millennium city main road in Kotugoda. This WRC is designed to handle a total flow of 7,250 m3/day. On average, the WRC is currently operating at 4,000 m3/day capacity, including sewage coming from 687 utility accounts and co-treatment of faecal sludge coming from surrounding unsewered areas.

Figure 2: System Map

P1: Sewage from households, commercial and industrial establishments

The system starts with households where wastewater is generated. Currently approximately 489 households [Including bulk meter connection of Millennium City, which has 820 units/ bulk meter connection of Nivasipura, which has 1,200 units] are connected to the sewer network. Additionally, wastewaters from 73 commercial and 118 industrial establishments are accommodated provided their wastewater meets the discharge standards to public sewer. This compliance is verified by the Water Reclamation Center Ja-Ela/Ekala) through field investigations.

T1: Sewer network and pumping stations

The wastewater is generated by consumers, flows under gravity to sewer manholes and collected at Pumping Stations (PSs). The sewer network is approximately 26km which lies in Ja-Ela/Ekala area. Additionally, the system is included with 226 nos. of manholes. This sewer network enables the transportation of wastewater to the treatment plant along three lifting Pumping stations. The pump stations are included of an underground sump, a pump house, a generator room (optional).

Manually cleaned coarse screens are available at inlet chamber before the pumping stations. The screen has free slot of 75 mm between the bars. The screen removes bigger things to prevent clogging of the pumps. The screenings are collected in a bucket-screen and subsequently lifted up transported to solar drying beds at WRC. The influent is collected in underground sump. The raw water levels are monitored using sensors and reported in real-time to the WRC.

Pump stations 2 (PS-2) is located besides temple road, PS-5 is located inside the Ekala industrial zone, and PS-4 is located nearby Ekala Madama junction. As an alternative source of power supply, generators were installed at PS-2, PS-5 and PS-4.

The sewage flows through sewers to pumping stations (PS-2, PS-4, and PS-5) under gravity. From PS-2 and PS-5, wastewater is pumped to two discharge manholes in PS-4 gravity network.

P2: Toilet and containment – storage/treatment with septic tanks and soakage pits

Currently Water Reclamation Center accepts faecal sludge from Ja-Ela Urban Council Limit.

T2: Conveyance of faecal sludge (FS) by vacuum trucks

The faecal sludge from household and commercial utilities is transported to WRC through private vacuum trucks, vacuum trucks belong to NWSDB and surrounding local authorities.

P2’and T3’: Pre-treatment of faecal sludge at WRC

There is a step screen (3mm fine screen) to remove screenings from the faecal sludge in faecal sludge receiver at the WRC. The screenings are washed, and dewatered in an area of the solar drying beds. After the screening of faecal sludge, liquid portion (Wastewater) is directed to the faecal sludge tank and subsequently pumped to the wastewater reception chamber at the WRC. The screen removes rags, paper and other large particles to prevent clogging in other equipment.

P3and T3’: Pre-treatment of wastewater

The wastewater is subjected to mechanical pretreatment. The pre-treatment system consists of reception chamber, two identical step screens (3mm fine screens installed parallely, a channel, two identical parallel constructed grit traps, a sand separator, a screen washer, grit container, collecting chamber, and split box. Followings are the steps in pre-treatment;

Reception chamber:

Wastewater from PS-4, Millennium city housing scheme, Niwasipura housing scheme, and air force base camp directly pump wastewater to the reception chamber in WRC. From the reception chamber, wastewater flows under gravity to subsequent treatment processes.

Screens, screen washer, and channel:

From the inlet chamber, the wastewater is pumped to two parallel mechanically rinsed fine screens. The screen is designed to remove solids greater than 3 mm. The screen removes rags, paper and other large particles to prevent clogging in other equipment. The screenings are automatically transported by the screw conveyor to the screening press zone containing a washing facility and dropped into containers. This reduces the volume of screening and the organic matter is washed out from the screenings and gets back into the wastewater flow. The washed screenings are dewatered in an area of the solar drying beds. In case of failure of the step screen, the water can bypass in a common overflow channel between the screens.

Grit traps, sand separator, grit container, collecting chamber, and split box:

The screened water is led to two mixed parallel grit traps, where sand and other heavy particles are removed to avoid abrasive wear on pumps and mechanical equipment. The grit traps are equipped with a frequency controlled submerged mixer, one in each grit trap, to allow only the heavy particles as sand and soil to settle while the suspended organic matter is kept in suspension for further treatment in the biological treatment process.

Settled grit is removed by a submerged grit pumps placed in each grit chamber. The settled grit is pumped to a sand separator. Reject water from the sand separator is led to the collecting chamber at the WRC. From the reception chamber and collecting chamber, there is a possibility to by-pass the biological treatment by opening an automatic penstock valve to the by-pass pipe. The by-pass flow is controlled by the flow meter placed in the split box in front of the biological treatment. In the split box the flow is divided into two streams. After the grit has been dewatered and rinsed in the sand separator, it is transported to a container.

P4: Secondary treatment: Biological treatment + Clarification

The process of secondary treatment includes biological treatment and sludge clarification. The biological treatment is carried out using the activated sludge method. The concept is to optimize the living conditions for the microorganisms naturally present in the wastewater as decomposers. The biological degradation that would normally occur in the receiving environment, consuming oxygen in the water, is instead completed in the treatment plant, thus preserving the recipient's environment.

At the Ja-Ela/Ekala wastewater treatment plant, the biological treatment is comprised of three zones: the anoxic zone, where denitrification occurs; the anaerobic basin; and the aerobic zone, where nitrification takes place.

### Anoxic Zone (Denitrification Basin)

### The pre-treated water entering the biological treatment first flows into the denitrification basins, where it is mixed with the return sludge recirculated from the clarifiers. Along with the return sludge, nitrate (NO3-N) is also recirculated from the clarifiers. The denitrification basins are anoxic, meaning the water contains no dissolved oxygen, but oxygen is present in the form of nitrate (NO3-N). Under anoxic conditions, nitrate is converted to nitrogen gas through denitrification according to the following formula.

It is important to maintain the concentration of dissolved oxygen below 0.5 mg/L in the anoxic basins; otherwise, the denitrification process will be hindered. A small amount of dissolved oxygen is always recirculated with the return sludge, so it is crucial that the concentration of dissolved oxygen in the anoxic basins is not unnecessarily high. The denitrification basins are equipped with one submerged mixer each to keep the sludge in suspension and ensure complete contact between the wastewater and the sludge.

### Anaerobic Zone (Anaerobic Basin)

Anaerobic conditions are defined by the absence of oxygen for microorganisms in the water. After passing through the denitrification basins, the water enters the anaerobic basins. The wastewater treatment process is designed to remove phosphorus. By exposing microorganisms to anaerobic conditions, an excess uptake of phosphorus occurs when the sludge is later aerated in the subsequent nitrification basins.

A key condition for biological phosphorus removal is the availability of a sufficient amount of easily degradable organic material in the anaerobic basins. This organic material comes from the influent raw wastewater. The amount of phosphorus removed depends on the amount of biodegradable organic material in the influent. To ensure enough easily biodegradable organic material for phosphorus reduction, it is possible to bypass a side stream from the split box directly to the anaerobic basins.

In the anaerobic basins, phosphorus-accumulating bacteria store organic material and release phosphorus, which results in an increase in dissolved phosphorus in the water. These organisms use the organic material as energy under aerobic conditions to store new phosphorus. Due to their growth, the organisms store more phosphorus under aerobic conditions than they release under anaerobic conditions. An activated sludge system with phosphorus-accumulating bacteria contains 3-5% phosphorus compared to an ordinary activated sludge system, where the phosphorus content is about 1.5%.

The anaerobic basins also act as a selector, improving the sludge's settling ability. Filament-forming bacteria are disadvantaged under anaerobic conditions. The anaerobic basins are equipped with a submerged agitator in each basin to ensure complete contact between the wastewater and the sludge. The agitator also keeps the sludge in suspension.

### Aerobic Zone (Nitrification Basin)

### Under aerobic conditions, the water contains dissolved oxygen. At a wastewater treatment plant, this condition is created by blowing air into the water. After passing through the anaerobic basins, the water continues into the aerobic basins for nitrification. Microorganisms use oxygen and release carbon dioxide and water. For their growth, these microorganisms use organic matter as an energy source, but they also need nutrients. The relationship between organic material and nutrients should be as follows:

In the aerobic basins, most of the organic nitrogen and ammonia nitrogen (NH4-N) from the influent water is converted to nitrate (NO3-N), a process known as nitrification.

The oxygen content should be adjusted to 1.5-2.0 mg/L and regularly monitored by the oxygen meters placed in the aerobic basins. Air is distributed to the wastewater through fine bubble rubber membrane diffusers fixed to the basin floor. These fine bubble aerators provide very efficient oxygen transfer, leading to lower energy consumption. Since the aeration system is the single biggest energy-consuming system at the wastewater treatment plant, its efficiency is crucial to minimizing energy use.

The oxygen supply system includes air blowers, oxygen meters, regulation valves, and a pressure transmitter. The blowers maintain constant pressure in the air pipes. When the load and thus the oxygen consumption changes, the oxygen meters signal the regulation valves to open or close. This causes the pressure in the air pipes to decrease or increase, prompting the blowers to adjust their speed to maintain constant pressure in the pipes.

Each aerobic basin is equipped with suspended solids (SS) meters, which control the excess sludge withdrawal and thus regulate the SS concentration in the basins.

### Clarification

The nitrification basins are followed directly by sedimentation basins for clarification. In the sedimentation basins, the activated sludge flocs are separated from the treated wastewater by gravity. The basins are equipped with traveling bridge siphon scrapers. The sludge is lifted by siphon action into a longitudinal sludge channel. From a small pump pit, the sludge is lifted by two frequency-controlled pumps and directed through two separate pipes to the beginning of the denitrification basins.

The return sludge flow to each train is measured with a flow meter, and the total return sludge flow is proportional to the inlet flow.

P5: Disinfection

To achieve the effluent requirements regarding fecal bacteria, the biologically treated effluent is disinfected by dosing sodium hypochlorite. The chlorination dosage is controlled by manually.

P6: Discharge of effluent (treated wastewater) to stream

The outfall of the facility is located at a river named as Dandugam Oya. Excess treated effluent is discharged to Dandugam Oya through a 710 mm diameter, 2.29 km long HDPE pumping main.

P6’: Reuse of effluent

Some part of the treated effluent is used to flushing of equipment such as belt-press machine and some part of the treated effluent is used to water the gardening area of water reclamation premises through sprinkler system.

T3: Conveyance of grit by dump truck

The grit from grit collection area (Container) is transported to grit storage area (land behind the solar drying beds (Within the water reclamation center premises) through a dump truck

T4’: Screenings management

The washed screenings is transported to solar drying beds first, and eventually incinerated at the grit and dried sludge storage area (land behind the solar drying beds within the water reclamation center premises) due to unavailability of sanitary landfills in the locality.

P7: Sludge treatment: Sludge storage + Polymer unit + Belt-filter press + Sludge collection container + Solar drying beds

When the SS concentration in the biological basins gets higher than the wanted, excess sludge is withdrawn from the return sludge flow by the opening of one of the two gate valves. The sludge is then led to either one of the two, parallel sludge storage basins equipped with submersible mixers and level meters, one of each in each basin. From the sludge storage basins, the sludge is pumped with two eccentric sludge pumps to a belt filter press for dewatering.

The sludge flow to the belt filter press is measured with a flow meter.  The dewatered sludge is transported from the press by screw conveyors to a sludge container. Polymer solution is dosed before the belt filter press with two frequency controlled eccentric screw pumps (one as stand by). The polymer solution is prepared in a polymer dissolving unit. Reject water from the belt filter press is led to the inlet pumping station.

T4: Conveyance of sludge cake by dump truck

The sludge cake from the belt-filter press machine is collected in sludge container and subsequently transported to the solar drying beds (Within the water reclamation center premises) through a dump truck.

T5: Conveyance of dried sludge by dump truck

The dried sludge (bio solids) from the solar drying beds are transported to the land behind the solar drying beds (Within the water reclamation center premises) through a dump truck.

P8: Grit and dried sludge storage area

Grit and dried sludge (bio solids) from the solar drying beds are transported to the land behind the solar drying beds (Within the water reclamation center premises).

P9: Usage of dried sludge (bio-solids) as a soil conditioner

Some part of dried sludge (bio-solids) is provided to the 3rd party, whom used dried sludge as soil conditioner in coconut cultivated land.

Figure 3: Flow Diagram

Based on the information obtained, the SSP team mapped the path of different waste flows through the sanitation system, from the point of generation to final use or disposal.

SS1=Receipt of sewage from households, commercial and industrial establishments

SS2= Conveyance of WW to WWTP via sewer network and pumping stations

SFS1=Faecal sludge collected in septic tanks and soak pits

SLF1=Liquid fraction that percolates from the pits

SFS2=Faecal sludge emptied into vacuum trucks and transported to the WWTP

SSWF1=Solid waste fraction that screened out from faecal sludge, washed, and then transported to solar drying bed

SSWF2=Solid waste fraction that screened out while going through the fine screen

SSF1=Sludge fraction separated from treated wastewater and collected in bin (After clarification/ and Belt filter press)

SSF2=Sludge fraction collected into dump truck from collection bin and transported to solar drying beds

SWW1= Secondary treated and clarified wastewater

SWW2= Disinfected wastewater (Disinfected using NaOCl) pumped into Dandugam Oya and dilute with river water

SWW3= Disinfected wastewater used for watering for gardening and flushing purposes

SGF1=Collected grit fraction transported, from grit container to grit storage area

SSWF3=Dried screening fraction from solar drying beds, transported to grit and dried sludge storage area and eventually incinerated

SSF3=Sludge fraction (sludge cake) dumped in and spread for treatment in solar drying beds

SSF4=Sludge fraction treated in solar drying beds transported to sludge storage area using dump trucks

SSFGF=Sludge fraction and grit fraction dumped and handled by spreading in storage area behind solar drying beds

SSF5=Dried Sludge fraction taken out by 3rd party for usage in coconut cultivated lands as a soil conditioner

## 2.2 Characterize System Flows

Figure 4: System Flow Diagram

Based on the information available, the SSP team used tool 2.1 to characterize the system flows and to collect key quantitative information, and information on the microbiological, physical and chemical hazards.

Table 4: Characterization of System Flow

| Sanitation Step | Description of the System Flow (Excreta-related flow such as ww or sludge, and other waste streams when relevant to sanitation system) | Key Information of the System Flow (Volume, flow, concentration, etc.) | Expected Variations (Seasonal variations or unusual events, such as accidentally mixed components or climate events) | Type of Potential Hazard (Biological, chemical, or physical) |
| --- | --- | --- | --- | --- |
| P1: Toilet and IC of houses, commercial, and industrial establishments | SS1=Receipt of sewage from households, commercial and industrial establishments | About 4000 m3 per day WW is collected. BOD could reach 300 mg/l | The sewage (Municipal WW) could contain faecal and urine (Black water), bathing water (Grey water), kitchen WW through grease traps, and chemicals from industrial connections | Biological Chemical |
| T1: Sewer network and pumping stations | SS2=Transfer (Conveyance) of WW from WW generation stage to WWTP via sewer network and pumping stations | About 4000 m3 per day WW is collected. BOD could reach 200 mg/l | Strength of WW is reduced due to dilution | Biological Physical Chemical |
| P2: Toilet and containment-storage/treatment with septic tanks and soak pits | SFS1=Faecal sludge collected in septic tanks and soak pits [Faecal sludge-solids and water that are collected in underground tanks] SLF1=Liquid fraction that percolates from the pits | About 100 m3 per day WW is collected. BOD could reach 600 mg/l - | The sludge could contain cleansing materials, menstrual hygiene products, sharp objects and other foreign material. It may also contain chemicals present in grey water. Depends on the soil type/ ground water table/Climate | Biological Physical Chemical |
| T2: Conveyance FS by vacuum trucks | SFS2=Faecal sludge emptied into vacuum trucks and transported to the WWTP | About 100 m3 of faecal sludge is received every day. | No expected variations. | Biological Physical |
| P2’ and T3’: Pre-treatment of faecal sludge at WRC | SSWF1=Solid waste fraction is screened out while pumping out the faecal sludge. Operators store screening waste in solar drying beds after washing. | About 2kg of solid waste is removed each time | Reduction of water content in washed screening waste | Biological Chemical |
| P3 and T3’: Pre-treatment of wastewater | SSWF2=Solid waste fraction is screened out while going through fine screen. Operators store screening waste in solar drying beds after washing. | About 5kg of solid waste is removed each time | Reduction of water content in washed screening waste | Biological Chemical |
| P4: Secondary treatment (Biological treatment and clarification) | SSF1=Sludge fraction separated from treated wastewater and collected in bin (After clarification/ and Belt filter press) | About 1000 kg of sludge is wasted each time | No expected variations. | Physical |
| T4: Conveyance of sludge cake by dump truck | SSF2=Sludge fraction collected into dump truck from collection bin and transported to solar drying beds | About 1000 kg of sludge is transported each time | No expected variations. | Biological Physical |
| P5: Disinfection | SWW1= Secondary treated and clarified wastewater | Around 8L of NaOCl is needed | No expected variations. | Chemical |
| P6: Discharge of effluent (treated wastewater) to stream | SWW2= Disinfected wastewater (Disinfected using NaOCl) pumped into Dandugam Oya and dilute with river water | About 4000 m3 per day WW is pumped. BOD of pumped WW is below 30 mg/l | Heavy rainfall leads to heavy dilution of wide range of constituents | Biological |
| P6’: Reuse of effluent | SWW3= Disinfected wastewater used for watering for gardening and flushing purposes | About 100 m3 per day WW is used. | With heavy rainfall, no need watering of gardens. In dry seasons, more WW is required for watering of garden areas. | Biological |
| T3: Conveyance of grit by dump truck | SGF1=Collected grit fraction transported, from grit container to grit storage area | About 1000 kg of grit is removed each time | No expected variations. | Biological |
| T4’: Conveyance of washed screenings | SSWF3=Dried screening fraction from solar drying beds, transported to grit and dried sludge storage area and eventually incinerated. | About 6kg of solid (Dried screenings) waste is incinerated each time | With heavy rainfall, solid waste/incinerated residues ends up in open drains/mix with surface or ground water. | Biological Chemical |
| P7 : Sludge treatment | SSF3=Sludge fraction (sludge cake) dumped in and spread for treatment in solar drying beds | About 10000 kg of sludge is dumped and spread each time | No expected variations. | Biological |
| T5: Conveyance of dried sludge by dump truck | SSF4=Sludge fraction treated in solar drying beds transported to sludge storage area using dump trucks | About 10000 kg of sludge is transported each time | No expected variations. | Biological Physical |
| P8: Grit and dried sludge storage | SSFGF=Sludge fraction and grit fraction dumped and handled by spreading in storage area behind solar drying beds | About 1000 kg of grit and 10000kg of sludge is dumped and spread each time | With heavy rainfall, faecal matter could ends up in open drains/mix with surface or ground water. | Biological |
| P9: Reuse of bio-solids | SSF5=Dried Sludge fraction taken out by 3rd party for usage in coconut cultivated lands as a soil conditioner | There are no data about quantities | With heavy rainfall, faecal matter could contaminate surface or ground water. | Biological |
| P10: Reuse of bio solids | SSF5=Dried Sludge fraction taken out by 3rd party for usage in coconut cultivated lands as a soil conditioner | About 850kg removed from one drying bed. | With heavy rainfall, fecal matter could contaminate surface or groundwater. | Biological |

## 2.3 Identify Exposure Groups

According to the 2018 WHO Guidelines on sanitation and health (WHO, 2018), the people most likely to be exposed to hazards during hazardous events at different steps of the sanitation service chain are as follows.

U   Sanitation system users	:  All people who use a toilet.

L Local community		:  People who live and/or work nearby (who are not necessarily users of the sanitation system) and may be exposed.

W Sanitation workers		:  All people (formally employed or informally engaged) responsible for maintaining, cleaning or operating (e.g. emptying, cleaning) a toilet or handling equipment (e.g. pumps, screeners, vehicles) at any step of the sanitation service chain.

WC Wider community	:   The wider population (e.g. farmers, communities in lower-lying areas) who are exposed to sanitation end-use products (e.g. through recreation or flooding) o consume products (e.g. fish, crops) that are produced using sanitation end-use products, intentionally or unintentionally. Sanitation end-use products include compost, fecal sludge and wastewater.

Depending on the sanitation service chain to which SSP applies, it might be necessary to treat the following exposure groups separately because they are exposed to very specific hazardous events during the end-use step (e.g. reuse in agriculture or aquaculture, consumption of products).

F Farmers			: People who use sanitation end-use products (e.g. untreated, partially treated or fully treated wastewater, biosolids, faecal sludge).

C Consumers			: Anyone who consumes or uses products (e.g. crops, fish, compost) that are produced using sanitation products.

The letters U, L, W, WC, F and C are used as symbols to identify the exposure groups in maps and tables, facilitating the health risk assessment in the subsequent modules.

The broad exposure groups (U, F, C, etc.) can be refined and defined into subgroups to aid the detailed hazard risk assessment, as shown in tool 2.2. For instance, the exposure group “U: sanitation system users” can be divided into U1: users of pit latrines, U2: users of flush toilets with a septic tank, and U3: users of toilets connected to the sewer system. It is important to estimate the number of individuals in each subgroup, how they come into contact with system flows (e.g. wastewater, excreta) and the frequency of exposure.

Table 5: Exposure Groups

| Symbol | Description |
| --- | --- |
| U1 | All people who use a toilet in sewer system in Ekala, Millennium City, Niwasi Pura, Air Force camp Ekala, Industrial zone and commercial establishments. |
| U2 | All people who use a toilet having onsite sanitation facilities in Ekala area. |
| U3 | All people who affected by flooding the onsite sanitation facility (septic tank and soakage pit) |
| W1 | All people who formally employed or informally engaged with cleaning or operating (e.g. emptying) a toilet or equipment (e.g. pumps, vehicles) at unsewered onsite toilets. |
| W2 | All people who employed in NWSDB and engaged in operation and maintenance work or equipment (e.g. pumps, vehicles) at any step of the sanitation service chain. |
| L1 | All the Local community who affected by contaminated groundwater due to infiltration from septic tanks and soak pits into shallow groundwater |
| L2 | All the Local community who affected by flooding the surrounding septic tanks and soakage pits. |
| L3 | All the Local community who affected by contaminated surface water or shallow ground water due to discharge of faecal sludge without treatment. |
| L4 | All the Local community who affected by ingesting waste water due to over flow from manholes. |
| L5 | All the Local community who affected by ingesting waste water due to submerging pump house 02 in rainy season. |
| L6 | All the Local community who affected by ingestion of storm water, contaminated with dried sludge during the raining period. |
| L7 | All the Local community who use the Water from Dandugam Oya below where effluents are discharged. |

Although some exposure groups, such as formal workers, are relatively easy to identify, others will be more difficult – for example, communities accessing nearby groundwater sources, seasonal and informal workers, and people living in informal settlements or immigrant populations. Demographics of the exposure groups, such as gender, age and potential social exclusion, should be noted. Climate change or climate variability may increase or decrease the frequency of exposure.

Figure 5: Exposure Group

Table 6: Characterization of Exposure Groups

| Sanitation Step | Exposure Group | Who are the Exposure Groups? (Description of these people) | How many are there? (Actual numbers, if known; otherwise estimate) | What are they doing? (Circumstances under which they might be exposed to hazards in the system flow) | What are they exposed to? (Which system flows and which types of hazards they have contact with) | How often are they exposed to this? (Exposure frequency: daily, weekly, once a year, etc.) |
| --- | --- | --- | --- | --- | --- | --- |
| P1: Toilet and IC of houses, commercial, and industrial establishments | U1 L2 | Users of flush toilets connected to sewer network through ICs Families live adjacent to the network | 675 utilities [Including bulk meter connection of 493 Domestics ( Including bulk meter connections of Millennium City, which has 820 units’ and Nivasipura, which has 1,200 units], 118 Industries, 73 Commercials, 2 Government institutes, and 1 Religious. 10,000 households | ICs are outside of the each premise. Children, Adults and workers are performing different activities in the vicinity. They usually have shallow dug wells, rather than deep tube wells | They could have contact with wastewater during overflows. Wells might contaminate with wastewater especially where seasonal high ground water table is presence, and distance to the well from unlined septic tank or soakage pits is short. They are exposed to microbial pathogens (Ex: E. Coli). | Overflow and contamination could happen every 2 years, but is more frequent during heavy rains. Seasonal, could be both during dry and rainy periods depending on situations |
| P2: Toilet and containment-storage/treatment with septic tanks and soak pits | U2 L1 | Users of flush toilets connected to septic tanks and soak pits in their properties Families living in areas where septic tank effluent and soak pits infiltrate to the ground water | 20,000 households (Around 60,000 people). About 35% are children 5,000 households (Around 15,000 people). About 25% are children | Septic tanks and soak pits are usually outside the house. Children play and adults perform different activities in the vicinity of the tank. They usually have shallow dug wells, rather than deep tube wells | They could have contact with wastewater during overflows from ICs or toilets. Wells might contaminate with ww especially where seasonal high ground water table is presence, and distance to the well from unlined septic tank or soakage pits are shallow. They are exposed to microbial pathogens (Ex: E. Coli). | Overflow and contamination could happen every 2 years, but is more frequent during heavy rains. Seasonal, could be both during dry and rainy periods depending on situations |
| T2: Conveyance FS by vacuum trucks | W1 | NWSDB or 3rd party (PS, UC, or private party etc.) vacuum truck operators | NWSDB – 4 operators 2 trucks PS – 12 operators 6 trucks UC – 4 operators 2 trucks Private – 147 operators 57 trucks | They open the underground tanks (Manhole covers or cover slabs), insert the hose of vacuum truck and empty the lined or unlined septic tanks and the soak pits. | They are in direct contact with fecal sludge, which contains pathogens. Possible bursts due to bio-gas formation in sealed septic tanks, especially where vent pipes have not been provided. | Every day Rare |
| T1: Sewer network and pumping stations | W2 | Network and pump stations O&M workers | 1 Officer, 2 drivers, 4 labours. | They usually contact with waste water, sludge, screenings etc. | They are direct contact with waste water, which contains pathogens. | Every day |
| P2’: Pre-treatment of fecal sludge at WRC | W2 | WRC Workers | 1 Officer, 3 labours | Cleaning of septic sludge receiver | They are direct contact with waste water and screenings which contains pathogens | Every day |
| P3: Pre-treatment of wastewater | W3 | WRC Workers | 1 Officer, 1 Technician, 2 labours | Cleaning of inlet channel, fine screens, screen conveyors, Grit traps, Grit pumps, and HP meter. | They are direct contact with waste water which contains pathogens | Every day |
| P4: Secondary treatment (Biological treatment and clarification) | W3 | WRC Workers | 1 Officer, 1 Technician, 2 labours | Cleaning of split box, DO meters, SS meter, Sides of anoxic tank, anaerobic tank, aerobic tank, Final clarifier, Outlet trays, etc. | They are direct contact with waste water which contains pathogens | Every day |
| T4: Conveyance of sludge cake by dump truck | W3 | WRC Workers | 2 Labours, 1 Lab Assistant, 1 Plant technician | Running belt press machine, Transport dewatered sludge to drying beds and open dumping area, | They are direct contact with waste water which contains pathogens. The water table of the ground floor can be polluted | 4 days per week |
| P5: Disinfection | W3 | WWTP Operators | 1 Plant technician | Pumping NaOCl to treated effluent | They are direct contact with NaOCl | Daily |
| P6: Discharge of effluent (treated wastewater) to stream | L4 W2 | People who consume fish (Fish caught from downstream of the treated effluent discharge location of Dandugam oya and lagoon | 500 people 2 Labours, 1 Lab Assistant | They eat fish without much care Outfall structure cleaning and Sampling. | Pathogens | Rare and Only in Rainy season Monthly |
| P6’: Reuse of effluent | W3 L3 | Labours who use the treated effluents (ww) to gardening the WRC premises Families living around Ekala WRC | 3 Labours 100 households | Gardening and landscaping work, Grass cutting, Plant watering using garden hose and sprinkles. When unloading the septage and disposal sludge on the ground | They can exposed to aerosol which can contain pathogenic microorganisms Odor smell can be inhale | Daily Daily |
| T3: Conveyance of grit by dump truck | W3 | WRC Workers | 2 workers | Empting the Grit collect container | They are direct contact with Grits which contains pathogens | weekly |
| T3’: Conveyance of washed screens | W3 | WRC Workers | 2 workers | Empting the washed fine screen container | They are direct contact with washed screenings which contains pathogens | Every two weeks |
| T4’: Conveyance of dried screenings | W3 | WRC Workers | 2 workers | Burning the dried screens | They are direct contact with Grits which contains pathogens and also can inhale toxic gasses | Monthly |
| P7: Sludge treatment | W3 | WRC Workers | 2 workers, Bob cat operator 1 Plant technician | Unloading the wet sludge to drying bed and operations | They are direct contact with dried sludge which contains pathogens. | Daily |
| T5: Conveyance of dried sludge by dump truck | W2 | Dry sludge carriers | 6 persons | Packing the dry sludge and transport | They are direct contact with dried sludge which contains pathogens | Monthly |
| P8: Grit and dried sludge storage | L3 W3 | Families living in the surrounding area of the Ekala WRC premises WRC Workers | 100 household | They live surrounding areas of WRC and some houses are close by the surface water canal | Mosquito breeding in grit and sludge storage area. Pathogens from partially treated sludge, grit, and toxic substances from the incinerated screenings might contaminate surface water canal and ultimately ground water (Probable contamination of shallow dug wells) | Often During rainy season |

## 2.4 Supporting Information

Regulatory Requirements Water quality standards

The National Environmental (Protection and Quality) regulations, No. 1 of 2008 published in the Gazette No. 1534/18 of February 1, 2008 gives the standards for discharge of wastewater or effluent into inland surface waters.

Table 7: Supporting Information

| Information Sources | Summary of Key Observations |
| --- | --- |
| Standards and regulations |  |
| Central environmental authority (CEA) effluent discharge standards 2022 | BOD, COD, TSS, pH, TDS, E. coli limit, Faecal Coliform (FC), Helminth eggs, |
| Information Related to system Management and Performance |  |
| Demographics and land-use patterns | Population near Ekala industrial area, Population near low-lying flood-prone areas where sanitation conditions are poor, Population where there are only basic sanitation available with onsite sanitation systems, |
| Changes relating to weather or other seasonal conditions | Demand for pit emptying also increases during heavy rainfall events, but flooding makes access to some areas difficult. Sewers overflow during severe rain events as a result of high flow and blockages caused by solid waste. |

# 3. HAZARDOUS EVENTS, ASSESSMENT OF EXISTING CONTROL MEASURES AND RISK EXPOSURE

## 3.1 Identification of Hazards and Hazardous Events

The Identification of hazards in sanitation safety planning is a critical step in ensuring the safety and effectiveness of wastewater management systems. This process involves systematically recognizing potential sources of contamination and risks associated with wastewater collection, treatment, and disposal. Common hazards include microbial pathogens such as bacteria, viruses, and parasites, which can cause waterborne diseases if not properly managed. Chemical hazards, including heavy metals and toxic compounds, may originate from industrial discharges and household chemicals, posing risks to both human health and the environment. Physical hazards, such as debris and blockages in the sewage system, can lead to system failures and overflows. Additionally, infrastructural vulnerabilities, like aging pipelines and treatment facilities, can exacerbate these risks.

Identifying these hazards requires a thorough assessment of the entire sanitation system. By pinpointing these hazards, sanitation safety plan can implement targeted control measures, enhancing the safety and reliability of the wastewater management system.

Table 8: Risk Definitions for Semi-quantitative risk assessment

|  | Descriptor | Description |
| --- | --- | --- |
| Likelihood (L) |  |  |
| 1 | Very Unlikely | Has not happened in the past and it is highly improbable it will happen in the next 12 months (or another reasonable period). |
| 2 | Unlikely | Has not happened in the past but may occur in exceptional circumstances in the next 12 months (or another reasonable period). |
| 3 | Possible | May have happened in the past and/or may occur under regular circumstances in the next 12 months (or another reasonable period). |
| 4 | Likely | Has been observed in the past and/or is likely to occur in the Next 12 months (or another reasonable period). |
| 5 | Almost certain | Has often been observed in the past and/or will almost certainly occur in most circumstances in the next 12 months (or another reasonable period). |

| Severity (S) |  |  |
| --- | --- | --- |
| 1 | Insignificant | Hazard or hazardous event resulting in no or negligible health effects compared with background levels. |
| 2 | Minor | Hazard or hazardous event potentially resulting in minor health effects (e.g. temporary symptoms of irritation, nausea, headache) |
| 4 | Moderate | Hazard or hazardous event potentially resulting in self-limiting health effects or minor illness (e.g. acute diarrhea, vomiting, upper respiratory tract infection, minor trauma). |
| 8 | Major | Hazard or hazardous event potentially resulting in illness or injury (e.g. malaria, schistosomiasis, food-borne trematodiases, chronic diarrhea, chronic respiratory problems, neurological disorders, bone fracture), and/or may lead to legal complaints and concern, and/or major regulatory noncompliance |
| 16 | Catastrophic | Hazard or hazardous event potentially resulting in serious illness or injury, or even loss of life (e.g. severe poisoning, loss of extremities, severe burns, drowning), and/or will lead to major investigation by regulator, with prosecution likely |

Table 9: Semi-Quantitative Risk Assessment Matrix

|  |  |  | Severity |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Insignificant | Minor | Moderate | Major | Catastrophic |
|  |  |  | 1 | 2 | 4 | 8 | 16 |
| Likelihood | Very Unlikely | 1 | 1 | 2 | 4 | 8 | 16 |
|  | Unlikely | 2 | 2 | 4 | 8 | 16 | 32 |
|  | Possible | 3 | 3 | 6 | 12 | 24 | 48 |
|  | Likely | 4 | 4 | 8 | 16 | 32 | 64 |
|  | Almost certain | 5 | 5 | 10 | 20 | 40 | 80 |
| Risk score R = L × S |  |  | <6 | 6-12 |  | 13-32 | >32 |

| Risk level | Low risk | Medium Risk | High Risk | Very High Risk |
| --- | --- | --- | --- | --- |

## 3.2 Identification and Assessment of Existing Control Measures

For each of the hazard and hazardous event identified. Existing control measures have been identified to mitigate the risk of such hazards and hazardous exposure events. The said control measures were then assessed on their effectiveness in reducing the risk of the exposure event.

Table 10: Risk Assessment

| COMPONENT | HAZARD IDENTIFICATION |  |  |  | EXISTING CONTROLS |  |  | RISK ASSESSMENT |  |  |  |  |  | COMMENTS JUSTIFYING RISK ASSESSMENT (Under current conditions, climate change scenarios, or effectiveness of the control) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | Under current conditions L=Likelihood; S=Severity; R=Risk (H=High; M=Medium; VH=Very high) |  |  |  | Under the most likely climate change scenarios + means increased risk - means decreased risk = means the same risk |  |  |
| Sanitation step | Hazardous event | Hazard | Exposure group | Number of people at risk | Description | Validation | Validation Effective/ Not Effective | L | S | Score (LxS) | R | Drought | More intense precipitation |  |
| P11: Toilet and IC of houses, commercial, and industrial establishments. | Ingestion after contact with wastewater in overflowing toilets or ICs | All microbial pathogens | U1 | 1000 | N/A | Visual observation | Not Effective | 3 | 4 | 12 | MR | - | + | This worsens during heavy rains, due to increase in infiltration. |
| P12: Toilet and IC of houses, commercial, and industrial establishments. | Add oil, grease, die, etc, with waste water collecting network. | Disturb the biological waste water treatment process. | L7 | Unknown | Randomly Collect samples from commercial establishments. | Sample Checking | Effective | 1 | 1 | 1 | LR | = | = | There is no effect on control on climate change, but depend on the activeness of the control measure. |
| P13: Toilet and IC of houses, commercial, and industrial establishments. | Receiving waste water over the limits of expected quality of the waste water. | Disturb the biological waste water treatment process. | L7 | Un known | Randomly check the samples from commercial establishments & check the waste water quality of the influent. | Sample Checking | Effective | 1 | 1 | 1 | LR | = | = | There is no effect on control on climate change, but depend on the activeness of the control measure. |
| P21: Toilet and containment-storage/treatment with septic tanks, soak pits and industrial establishments. | Ingestion after contact with excreta due to blocking. | All microbial pathogens | U2 | Un known | Properly functioning flush toilets with water supply. Not enter solid waste to the sewer system. | Visual observation/ Survey | Effective | 3 | 4 | 12 | MR | - | + |  |
| P22: Toilet and containment-storage/treatment with septic tanks, soak pits and industrial establishments. | Ingestion after contact with excreta due to overflowing. | All microbial pathogens | U2 | Un known | Empting the pits by manual ways Periodically empting the pits by using the Vacuum Trucks. | Visual observation | Effective |  |  |  |  |  |  |  |
| P23: Disposal of liquid fraction by infiltration | Ingestion of contaminated groundwater due to infiltration from septic tanks and soak pits into shallow groundwater | Faecal pathogens | L1 | 12000 | Safe distance from wells would have to be considered. | Field visits | Not Effective | 5 | 4 | 20 | HR | + | + | Likelihood of groundwater use is expected to increase during drought periods. Severity will increase with more and prolonged flooding due to climate change. Consideration should be given to vulnerable communities that may have reduced ability to find alternative water sources. |
| P24: Toilet and containment-storage/treatment with septic tanks and soak pits | Ingestion after contact with wastewater from flooding onsite systems due heavy rains and storm water logging. | All microbial pathogens | U3 | 30000 | Present problems of septic tanks and soak pits. | Field visits and interviews | Not Effective | 3 | 4 | 12 | MR | - | + | Likelihood and severity will increase with heavy rainfall and flooding. |
|  |  |  | L2 | 5000 |  |  | Not Effective | 3 | 2 | 6 | LR | - | + | The localized problem of septic tank damage becomes a community problem with flooding, affecting others in the vicinity. |
| P25: Disposal of faecal sludge without treatment or Deep Row Entrenchment | Ingestion after contact with faecal sludge discharged without treatment, contaminated surface water or shallow ground water | All microbial pathogens | L3 | 1500 | Nil | NA | Not Effective | 3 | 4 | 12 | MR | = | + | Currently, risk is both during dry and rainy periods depending on situations. And generally higher risk during heavy rains. |
| T21: Conveyance of FS by vacuum trucks | Ingestion after contact with raw sewage during vacuum tanker operation | All microbial pathogens | W1 | 50 | Wearing gloves during work | Visual Observation | Effective | 3 | 4 | 12 | MR | = | + | Wearing gloves and hand washing with soap or detergent after emptying is not widely practiced. In flooding conditions, the likelihood will increase. |
| T11: Conveyance of sewer through the network. | Waste water, over flow from the man holes and flow along the road due to the blockage in the network. | All microbial pathogens | L4 | Unknown | Proper maintenance of sewage network system and proper storm water management prevent the overflow of waste water. | Visual observation | Effective | 5 | 2 | 10 | MR | - | + | This worsens during heavy rains, due to increase in overflow. |
| T12: Conveyance of sewer through the network. | Submerge the pumping station 02 (PS 02) in rainy season and contaminate the storm water with sewer water. | All microbial pathogens. | W2 | 6 | clean the drains | Visual observation | Some Extend Effective | 5 | 4 | 20 | HR | - | + | During the rain the risk will be increase |
|  |  |  | L5 | 500 |  |  |  | 5 | 4 | 20 | HR | - | + | During the rain the risk will be increase |
| T13: Conveyance of sewer through the network. | Submerge the pumping station 04 (PS 04) in rainy season and contaminate the storm water with sewer water. | All microbial pathogens | W2 | 5 | Cleaning the Drains | Visual observation | Some Extend Effective | 5 | 2 | 10 | MR | - | + | During the rain the risk will be increase |
| T14: Conveyance of Sewer through the network and pumping stations | Ingestion after contact with excreta during the repair work of blocking pipe lines and damaged pipe lines. | All microbial pathogens | W2 | 10 | Wearing personal protective equipment during the work | Visual observation | Some Extend Effective | 5 | 3 | 15 | HR | = | = | No effect from climate change. |
| P31 Inlet channel cleaning due to sand trapping | Ingestion after contact with sewer while entering or falling into inlet channel. | All microbial pathogens, Injury to body. | W2 | 6 | Use PPE/SOP and disinfection soap | observation and training | Some Extend Effective | 4 | 1 | 4 | Low risk | - | + | During the rain the risk will be increase |
| P32 Fine screen cleaning due to blocking. | Ingestion after contact with sewer while entering or falling into inlet channel | All microbial pathogens, Injury to body. | W2 | 3 | Use PPE/SOP and disinfection soap | observation and training | Effective | 4 | 1 | 4 | Low risk | - | + | During the rain the risk will be increase. |
| P41 Inlet channel PH sensor cleaning due to some deposits. | Ingestion after contact with sewer while cleaning | All microbial pathogens. | W2 | 1 | Use PPE/SOP and disinfection soap | Training | Effective | 3 | 1 | 3 | Low risk | = | = | No effect from climate change. |
| P42 Grit chamber cleaning for preventive maintenance | Ingestion after contact with sewer while entering or falling into Chamber. | All microbial pathogens. | W2 | 5 | Use PPE/SOP and disinfection soap | observation and training | Entering –Effective Falling – Not Effective | 4 | 1 | 4 | Low risk | - | + | During the rain the risk will be increase |
|  |  |  | W2 | 1 | Use PPE/SOP and disinfection soap | observation and training |  | 3 | 1 | 3 | Low risk | - | + |  |
| P43 Mixer preventive maintenance work in anoxic and anaerobic area. | Ingestion after contact with sewer while cleaning, or falling in to the tank | All microbial pathogens, Injury to body. | W2 | 2 | Use PPE/SOP and disinfection soap | observation and training | Entering –Effective Falling – Not Effective | 3 | 1 | 3 | Low risk | = | = | No effect from climate change. |
| P44 Mixer cleaning in grit chambers due to congestion | Ingestion after contact with sewer while cleaning, or falling in to the tank | All microbial pathogens, Injury to body. | W2 | 2 | Use PPE/SOP and disinfection soap | observation and training | Entering –Effective Falling – Not Effective | 3 | 1 | 3 | Low risk | = | = | No effect from climate change. |
| P45 Mixer cleaning in septic sludge storage tank due to congestion | Ingestion after contact with sewer while cleaning, or falling in to the tank | All microbial pathogens, Injury to body. | W2 | 3 | Use PPE/SOP and disinfection soap | observation and training | Entering –Effective Falling – Not Effective | 3 | 1 | 3 | Low risk | = | = | No effect from climate change. |
| P46 Septic sump cleaning due to sand trapping | Ingestion after contact with sewer while entering or falling into the sump. | All microbial pathogens, Injury to body. | W2 | 6 | Use PPE/SOP and disinfection soap | observation and training | Entering –Effective Falling – Not Effective | 4 | 2 | 8 | MR | - | + | During the rain the risk will be increase |
|  |  |  | W2 | 1 | Use PPE/SOP and disinfection soap | observation and training |  | 3 | 2 | 6 | Low risk | - | + |  |
| P47 Septic Pump and Grit Pump Cleaning For Preventive maintenance. | Ingestion after contact with sewer while cleaning, or falling in to the tank | All microbial pathogens, Injury to body. | W2 | 2 | Use PPE/SOP and disinfection soap | observation and training | Entering –Effective Falling – Not Effective | 3 | 1 | 3 | Low risk | = | = | No effect from climate change. |
| P48 Septic sump and sludge tank cleaning due to sand trapping | Inhale toxic gasses and possible asphyxiation, when enter to the tanks for cleaning. | All microbial pathogens, Injury to body. | W2 | 6 | Use PPE/SOP and disinfection soap | observation and training | Entering –Effective Falling – Not Effective | 2 | 8 | 16 | HR | - | + | During the rain the risk will be increase |
|  |  |  | W2 | 1 | Use PPE/SOP and disinfection soap | observation and training |  | 3 | 2 | 6 | Low risk | - | + |  |
| P49 Return sludge channel cleaning due to sludge deposit. | Ingestion after contact with sewer while entering or falling into inlet channel | All microbial pathogens, Injury to body. | W2 | 6 | Use PPE/SOP and disinfection soap | observation and training | Entering –Effective Falling – Not Effective | 3 | 1 | 3 | Low risk | = | = | No effect from climate change. |
|  |  |  | W2 | 1 | Use PPE/SOP and disinfection soap | observation and training |  | 2 | 1 | 2 | Low risk | = | = |  |
| P410 Return sludge channel cleaning due to sludge deposit. | Ingestion after contact with sewer while entering or falling into inlet channel | All microbial pathogens, Injury to body. | W2 | 6 | Use PPE/SOP and disinfection soap | observation and training | Entering –Effective Falling – Not Effective | 3 | 1 | 3 | Low risk | = | = | No effect from climate change. |
| P411 Return sludge pump cleaning due to blocking. | Ingestion after contact with sewer while entering or falling into inlet channel | All microbial pathogens, Injury to body. | W2 | 2 | Use PPE/SOP and disinfection soap | observation and training | Entering –Effective Falling – Not Effective | 3 | 1 | 3 | Low risk | = | = | No effect from climate change. |
| P412 Air diffuser cleaning due to blocking. | Ingestion after contact with sewer while cleaning and falling and sinking in aeration tank. | All microbial pathogens, Injury to body. | W2 | 25 | Use PPE/SOP and disinfection soap | observation and training | Entering –Effective Falling – Not Effective | 4 | 2 | 8 | MR | = | = | No effect from climate change. |
| P413 Scum collecting channel cleaning. | Ingestion after contact with sewer while cleaning and falling and sinking in sedimentation tank. | All microbial pathogens, Injury to body. | W2 | 3 | Use PPE/SOP and disinfection soap | observation and training | Entering –Effective Falling – Not Effective | 4 | 1 | 4 | Low risk | = | = | No effect from climate change. |
| P414 O2 sensor cleaning in aeration tank due to some deposits. | Ingestion after contact with sewer while cleaning | All microbial pathogens. | W2 | 1 | Use PPE/SOP and disinfection soap | Training | Effective | 3 | 1 | 3 | Low risk | = | = | No effect from climate change. |
| P415 SS sensor cleaning in aeration tank due to some deposits. | Ingestion after contact with sewer while cleaning | All microbial pathogens. | W2 | 1 | Use PPE/SOP and disinfection soap | Training | Effective | 3 | 1 | 3 | Low risk | = | = | No effect from climate change. |
| P416 Outlet water SS channel cleaning. | Ingestion after contact with sewer while cleaning | All microbial pathogens. | W2 | 2 | Use PPE/SOP and disinfection soap | observation and training | Effective | 3 | 1 | 3 | Low risk | = | = | No effect from climate change. |
| P417 Outlet sump cleaning. | Ingestion after contact with sewer while cleaning | All microbial pathogens. | W2 | 3 | Use PPE/SOP and disinfection soap | observation and training | Effective | 3 | 1 | 3 | Low risk | = | = | No effect from climate change. |
| P418 Outfall structure cleaning. | Ingestion after contact with sewer while cleaning and falling and sinking in river. | All microbial pathogens. Injury to body. | W2 | 2 | Use PPE/SOP and disinfection soap | observation and training | Entering –Effective Falling – Not Effective | 3 | 1 | 3 | Low risk | = | = | No effect from climate change. |
| P419Sludge Storage Tank Cleaning | Ingestion after Contact with sewer while cleaning or Falling in to the tank | All microbial pathogens, Injury to body. | W2 | 6 | Use PPE/SOP and disinfection soap | observation and training | Entering –Effective Falling – Not Effective | 4 | 2 | 8 | MR | = | = | No effect from climate change. |
|  |  |  | W2 | 1 | Use PPE/SOP and disinfection soap | observation and training |  | 3 | 2 | 6 | Low risk | = | = | No effect from climate change. |
| P420 Belt Press machine operation and cleaning | Ingestion after Contact with sewer while cleaning or Falling from belt machine. | All microbial pathogens, Injury to body. | W2 | 2 | Use PPE/SOP and disinfection soap | observation and training | Effective | 3 | 1 | 3 | Low risk | = | = | No effect from climate change. |
| P421 Compost filter cleaning and refilling filter media, | Ingestion after contact with sewer while cleaning, | All microbial pathogens, | W2 | 5 | Use PPE/SOP and disinfection soap | observation and training | Effective | 3 | 1 | 3 | Low risk | = | + | During the rain the risk will be increase |
| P422: Secondary Treatment Process in the settling tank. | Due to poor performance in sludge scraper treatment process will be disturbed and Water of Dandugam Oya is contaminated with partially treated waste water. | All microbial pathogens | L7 | Unknown | Preventive maintenance and keeping standby gear Box and other necessary equipment. | Visual observation normally once a six month, wheels should be replaced. | Effective | 3 | 4 | 12 | MR | = | = | No effect from climate change. |
| P51: Chlorine container replacing. | Body contact with liquid chlorine and Inhale of chlorine gas. | Injury to body. Breathing complications | W2 | 2 | Use PPE/SOP and disinfection soap | observation and training | Effective | 3 | 1 | 3 | Low risk | = | = | No effect from climate change. |
| P91: Disposal of dried sludge | Ingestion of Storm water, contaminated with dried sludge during the raining period. | All microbial pathogens, | W2 | 10 | N/A | Visual observation | Effective | 4 | 4 | 16 | HR | = | + | During the rain the risk will be increase |
| P101: Disposal of dried screenings | Due to burning of screenings, toxic gasses may formed. | Possibility of asphyxiation, caused by toxic gasses. | W2 | 2 | N/A | N/A | Not Effective | 4 | 4 | 16 | HR | = | = | In rainy seasons, it is difficult to burn the screens. Then screens will pile up at the site. |

## 3.3 Assessment and Prioritization of Risk Exposure

The risks were assessed based on its likelihood and severity. The computed level of risk and likelihood equates to the ranking of risks. Where in the risk level was identified. Furthermore, the risk category which require additional control or improvements were listed and described here to highlight the actions to be taken to reduce the risks.

Table 11: Priorities Hazardous Event with High Risk

| Reference No. | Sanitation step | Hazardous event | Exposure group | Number of people at risk | Risk | Projection of changers in risk with climate change scenarios | Priority Given |
| --- | --- | --- | --- | --- | --- | --- | --- |
| P23 | Disposal of liquid fraction by infiltration | Ingestion of contaminated groundwater due to infiltration from septic tanks and soak pits into shallow groundwater | L1 | 12000 | HR | During the rain the risk will be increase | High |
| T12 | Conveyance of sewer through the network. | Submerge the pumping station 02 (PS 02) in rainy season and contaminate the storm water with sewer water. | W2 | 6 | HR | During the rain the risk will be increase | High |
|  |  |  | L5 | 500 | HR | During the rain the risk will be increase | High |
| T14 | Conveyance of Sewer through the network and pumping stations | Ingestion after contact with excreta during the repair work of blocking pipe lines and damaged pipe lines. | W2 | 10 | HR | No effect from climate change. | High |
| P48 | Septic sump and sludge tank cleaning due to sand trapping | Inhale toxic gasses and possible asphyxiation, when enter to the tanks for cleaning. | W2 | 6 | HR | No effect from climate change. | High |
| P91 | Disposal of dried sludge | Ingestion of Storm water, contaminated with dried sludge during the raining period. | W2 | 10 | HR | During the rain the risk will be increase | High |
| P101 | Disposal of dried screenings | Due to burning of screenings, toxic gasses may formed. | W2 | 2 | HR | In rainy seasons, it is difficult to burn the screens. Then screens will pile up at the site. | High |

# DEVELOPMENT AND IMPLEMENTATION OF INCREMENTAL IMPROVEMENT PLAN

## 4.1 Consideration of Options to Control Identified Risks

In this step, variety of ways to control risks, including technology upgrades, changes in management and operation, behavior change measures, and policy and regulatory measures, covering all steps of the sanitation chain were considered.

Table 12: Control Option for Conveyance of Sewer through the Network and Pumping Station

| Step of the sanitation service chain: T12: Conveyance of Sewer through the network and pumping stations |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description of hazardous event: Submerge the pumping station 02 (PO 02) in rainy season and contaminate the storm water with sewer water. |  |  |  |  |  |
| Exposure group: About 06 workers who engaged with maintenance works and about 500 workers around the PS 02 area. |  |  |  |  |  |
| IMPROVEMENT OPTIONS |  |  |  |  |  |
| Option | Effectiveness | Level of resources | Effectiveness under climate change scenarios | Comments/discussion | Priority for improvement plan |
| Clean the Canal system near the PS 02 area. | Medium | Low | During the rainy season continues cleaning is required. | The support of the Ja Ela Pradeshiya Sabha has been taken to clean the drainage system. | Short Term |
| Raise the ground level of the pump house. | High | low | Effective | Existing ground level of the pump house is lower than the road level. Therefore water is accumulated and staged. | Medium Term |
| Raise the boundary wall of the pump house as a retaining wall. (wall of the existing drainage) | High | Medium | Effective | Parallel with the drainage cleaning flooding will be able to minimize. | Medium Term |

Table 13: Control Option for Conveyance of Sewer through the Network and Pumping Stations

| Step of the sanitation service chain: T14: Conveyance of Sewer through the network and pumping stations |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description of hazardous event: Ingestion after contact with excreta during the repair work of blocking pipe lines and damaged pipe lines. |  |  |  |  |  |
| Exposure group: About 10 workers who engaged with maintenance works. |  |  |  |  |  |
| IMPROVEMENT OPTIONS |  |  |  |  |  |
| Option | Effectiveness | Level of resources | Effectiveness under climate change scenarios | Comments/discussion | Priority for improvement plan |
| Implementation of regular preventive maintenance programs covering the network. (Collecting network has divided in to four zones and monthly one zone is cleaned.) | High | Medium | Effective | NWSDB, Preventive maintenance will reduce the high risk with minimum cost. | Short Term |
| Identify the highly vulnerable areas and refurbishment the network. | High | High | In rainy season difficult to engaged |  | Medium Term |
| Encourage to ware personal protective equipment during the maintenance work. | Medium | Low | Effective | NWSDB provide necessary PPE to the workers. | Short Term |

Table 14: Control Option for Septic sump and Sludge tank cleaning

| Step of the sanitation service chain: P48: Septic sump and sludge tank cleaning remove the sand and scum. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description of hazardous event: inhale toxic gasses and possible asphyxiation, when enter to the tanks for cleaning. |  |  |  |  |  |
| Exposure group: About 06 people engaged in maintenance work in Ekala WRC. |  |  |  |  |  |
| IMPROVEMENT OPTIONS |  |  |  |  |  |
| Option | Effectiveness | Level of resources | Effectiveness under climate change scenarios | Comments/discussion | Priority for improvement plan |
| Use toxic gasses detecting technics before enter in to the tanks( gas detectors) | Medium | Low | Effective | When there is not available enough O2, (CH4, NH4 concentration is high) lightning will not be occurring. | short Term |
| Organizing awareness programs about the safety measures should be followed. | Medium | Low | Effective | Periodically awareness programs are schedule | short Term |
| Follow the SOP in maintenance work. | Medium | Medium | Effective | Training on SOPs should be given. SOPs should be displayed in the site and it should be in Sinhala language. | Short Term |
| Wearing personal protective equipment during the maintenance works. | High | Medium | Effective | NWSDB provide necessary PPE to the workers. | Sort Term |

Table 15: Control Option for Disposal of Dried Sludge

| Step of the sanitation service chain: P91: Disposal of Dried Sludge |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description of hazardous event: Ingestion of Storm water, contaminated with dried sludge during the raining period. |  |  |  |  |  |
| Exposure group: Local community is exposer for the risk but nor clear idea about the number of people at risk. |  |  |  |  |  |
| IMPROVEMENT OPTIONS |  |  |  |  |  |
| Option | Effectiveness | Level of resources | Effectiveness under climate change scenarios | Comments/discussion | Priority for improvement plan |
| Dumping dried sludge corner of the land in the treatment plant and make a bunch of earth about two feet height and cover the dried sludge with a thick polythene to avoid/minimize contamination of dried sludge with storm water. | Low | Low | Less Effective | In dry period it there is no issue. But with the rainy period the situation become more critical to manage. | Immediate |
| Use a backhoe loader and collect the dried sludge have spreaded throughout the treatment plant. | Medium | Medium | Less Effective | Drying bed capacity is not enough. Therefore dried sludge is stored in open area outside of the solar drying beds. | Immediate |
| Display board to aware about, availability of dried sludge free of charge to use as a fertilizer. | Low | Low | Less Effective | There is no proper path to dispose the dried sludge | Short Term |
| Call tender for remove the Piled sludge at Ekala WRC. | High | Medium | Effective | Can’t insure whether it is dispose safely to the environment. | Immediate |
| Construct another set of solar drying bed. | High | High | Less Effective | Solar drying beds are more suitable than the use of exhaust fans. | Long Term |

Table 16: Control Option for Disposal of Dried Screen

| Step of the sanitation service chain: P101: Disposal of Dried Screens |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description of hazardous event: Possibility of asphyxiation, caused by toxic gasses. |  |  |  |  |  |
| Exposure group: About 02 people engaged in maintenance work in Ekala WRC. |  |  |  |  |  |
| IMPROVEMENT OPTIONS |  |  |  |  |  |
| Option | Effectiveness | Level of resources | Effectiveness under climate change scenarios | Comments/discussion | Priority for improvement plan |
| Aware consumers not to dispose solid waste to the sewer network. | High | Low | No effect due to the climate change. | It is difficult to change the attitudes of the Consumers. Not practicable. If it is possible, it is the better solution. | Long Term |
| Construct an incinerator in the Ekala WRC. | Medium | High | Effective in some extend | Air Pollution will not be reduced, but effect to the workers in the Ekala WRC will be reduced. | Medium Term |
| Hand over the solid waste to the Central Environmental Authority for sanitary land filling. | Medium | Medium | Effective | Should be discussed with the CEA | Immediate |
| Hand over solid waste to the energy generation project. | High | Medium | Effective | Not Practical because there is no sufficient a quantity of solid waste and no energy generation projects by solid waste near the Ekala area. | Long Term |

Table 17: Climate Adaptation for a Specific Sanitation Step

| Sanitation Technology | Most Probable Climate Change Scenario | Effect on Sanitation System | Hazardous Event | Adaptation Option |
| --- | --- | --- | --- | --- |
| Waste water treatment | More intensive storm | Disturb the treatment process by diluting the waste water with Storm water. | water/partially treated waste water diverted to the Dandugam Oya and contaminate the river water and effect to the users of river down | Drainage system of the area should be improved Controlling infiltration reduce energy consumption |
| Waste water treatment. | More intensive storms | It disturbs the sludge drying process by solar power. | wet sludge piles up in the premises | Increased drying bed area. Eco friendly sludge disposal method to be introduced |

4.2 Development of an Incremental Improvement Plan

The incremental improvement plan was prepared prioritizing the control measures which did not required major funds or time for the next 3 years

Table 18: Improvement Plan

|  | Improvement measure | Cost Rs. | Source of funds | Lead organization | Coordinator |  | 2024 |  |  |  |  |  |  |  |  |  |  |  |  | 2025 |  |  |  |  | 2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | Q1 |  | Q2 | Q3 | Q4 | Q1 |  | Q2 | Q3 | Q4 |
| T1: Conveyance of sewer through the network. |  |  |
|  | Clean the drainage system near the PS 02 area. | 30,000.00 | O&M | NWSDB Manager office (Ja Ela/Ekala) | OIC (Network) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Clean the drainage system near the PS 02 area. |  |  | Ja Ela Pradeshiya Sabha | Regional Manager (JaEla) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Raise the ground level of the pump house. | 700,000.00 | RH/O&M | NWSDB Manager office (Ja Ela/Ekala) | OIC (Network) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Raise the boundary wall of the pump house as a retaining wall. (wall of the existing drainage) | 1,200,000.00 | RH | NWSDB Manager office (Ja Ela/Ekala) | OIC (Network) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Implementation of regular preventive maintenance programs covering the network. | 100,000.00 | O&M | NWSDB Ekala WRC | OIC (Network) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Repair Sewerage pipe line at IDB near the Maithree Mawatha. | 6,336,000.00 |  | NWSDB Ekala WRC | OIC (Network) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Leak Repair along the Raja Mawatha | 20,000,000.00 | RH | NWSDB Ekala WRC | OIC (Network) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Raising of manholes of sewer network. | 3,202,166.00 | RH | NWSDB Ekala WRC | OIC (Network) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Purchase sewer pipe line inspection camera system | 3,658,000.00 | RH | NWSDB Ekala WRC | Engineer (O&M) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Identify the highly vulnerable areas and refurbishment the network. | 100,000.00 | O&M | NWSDB Ekala WRC | Engineer (O&M) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Encourage to wear personal protective equipment during the maintenance work. | 10,000.00 | O&M | NWSDB Ekala WRC | OIC (Network) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| P5: Secondary Treatment Process. |  |  |  |  |  |
|  | Wearing personal protective equipment during the operation. | 10,000.00 | O&M | NWSDB Ekala WRC | OIC (Ekala) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Purchasing toxic gasses detecting equipment. | 2,000,000.00 | O&M | NWSDB Ekala WRC | OIC (Ekala) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Organizing awareness programs about the safety measures should be followed. | 30,000.00 | O&M | NWSDB Ekala WRC | OIC (Ekala) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Training on SOPs should be given. | 30,000.00 | O&M | NWSDB Ekala WRC | OIC (Ekala) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | SOPs should be displayed in the site and it should be in Sinhala language. | 1,000.00 | O&M | NWSDB Ekala WRC | OIC (Ekala) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Wearing personal protective equipment during the maintenance works. | 100,000.00 | O&M | NWSDB Ekala WRC | OIC (Ekala) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| P9: Disposal of Dried Sludge |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Use a backhoe loader and collect the dried sludge spreaded throughout the treatment plant. | 200,000.00 | O&M | NWSDB Ekala WRC | OIC (Ekala) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Removing piled up sludge from the Ekala water reclamation center | 1,000,000.00 | O&M | NWSDB Ekala WRC | OIC (Ekala) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Display board to aware about, availability of dried sludge free of charge to use as a soil conditioner. | 2500.00 | O&M | NWSDB Ekala WRC | OIC (Ekala) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| P101: Disposal of Dried Screenings |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Hand over the solid waste to the Central Environmental Authority for sanitary land filling. | 100,000.00 | O&M | NWSDB Ekala WRC | OIC (Ekala) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

## 4.3 Implementation of the Improvement Plan

SSP implementation was challenging, and building upon the initial commitments and motivation of all stakeholders required continuous follow-up. The SSP team leader organized meetings with the SSP task forces on a regular basis to review progress and discuss challenges.

# MONITORING OF CONTROL MEASURES AND VERIFICATION OF PERFORMANCE

## 5.1 Definition and Implementation of Operational Monitoring

Monitoring and verification plans were developed using the Tool 5.1. Tool 5.1 helped to decide which control measures should be monitored to ensure each operation.

Table 19: Operational Monitoring Overview

| Sanitation step | Control measures for a detailed operational monitoring plan |
| --- | --- |
| P1: Toilet and IC of houses, commercial, and industrial establishments | - Awareness-raising campaign targeting the industrial establishments to prevent entering solid particles, dye, heavy metals, storm water to the sewer network. - Randomly collect samples from industrial establishments without prior notice and testing |
| T1: Conveyance of Sewer through the network and pumping stations | - Implementation of regular preventive maintenance programs covering the network including manholes cover and lock greasing etc. - Recover the blockages and leaks within 48 hours. - Encourage to ware personal protective equipment during the maintenance work. - Use ventilator to remove the toxic gases such as Ammonia, Methane, and Sulphur dioxide in the manhole. - Use gas detectors during the repair and maintenance works in manholes. - Clean the drainage system near the pump house 02 area. - Clean the drainage system near the pump house 04 area. - Laying of bypass line when the existing line is blocked/ damaged/ abandoned. - Repair the decay manholes. |
| T2: Conveyance of FS by vacuum trucks | - Testing quality of the fecal sludge before discharging (pH, colour, oil, grees, odor etc.) - Encourage safe disposal of fecal sludge by monitoring the continuous disposal of fecal sludge and cancelling the registration, who do not unload the fecal sludge for one year period. - Wearing personal protective equipment during the operation. |
| P4: Secondary Treatment Process. | - Quality of influent and the effluent are checked by sample testing in inlet, Anoxic tank, anaerobic tank, and Aerobic tank and in the final clarifier by daily, and full test done by weekly in the plant laboratory. - Monthly samples are sent to Ambathale laboratory test for heavy metals. - Remove the excess sludge to maintain the SS level between the 2500mg/l to 3500mg/l in the final clarifier. - Monitor the oxygen level in the aeration tank by sensors. - Wearing personal protective equipment during the operation and maintenance. - Use ventilator to remove the toxic gases such as Ammonia, Methane in the grit chambers, septic sludge storage tank, excess sludge storage tank, outlet sump, etc. - Use gas detectors before enter to the grit chambers, septic sludge storage tank, excess sludge storage tank, outlet sump, etc. - Maintain the odor removal system in the plant. - Place safety ring buoyance at secondary treatment area. - Inspect/check current condition of the steel flat forms/checker plates (corrosion/damagers/decays) annually. |
| P5: Disinfection | - Maintain stocks of Sodium Hypochlorite for one month period (300kg) to ensure that the strength of the chemicals are not decreased. |
| P6: Discharge of effluent (treated wastewater) to Dandugam Oya | - Sample testing daily for colour in the final clarifier. - Sample testing weekly for pH, Temperature, DO, TSS, Colour, BOD, COD, TDS, RCl in the final clarifier. - Sample test at the river outfall annually for pH, Temperature, DO, TSS, Colour, BOD, COD,TDS, RCl |
| P6’: Reuse of effluent for gardening purposes | - Display notice boards to aware that water is not suitable for drinking purpose. |
| P9: Disposal of Dried Sludge | - Dry sludge test for heavy metals done one a year period. - Providing dried sludge free of charge to the farmers who cultivate coconut. |

Table 20: Operational Monitoring Plan for P1; Toilet and IC of house, commercial, and industrial establishment

| Operational monitoring plan for: Avoid adding exceeded heavy metal concentrations to the treatment plant. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Operational limits | Operational monitoring of the control measure |  | Corrective action when the operational limit is exceeded |  |
| Industrial Establishments who discharge the industrial waste water to Ekala water reclamation center should not discharge Greece, oil, heavy metals and storm water to the system. | What is monitored? | Concentration of heavy metals, Greece, oil in the wastewater. | What action is to be taken? | Inform to the factory owners in writing with a copy to the CEA to stop the dispose such waste water to the NWSDB sewer network and do the pretreatment. |
|  | How is it monitored? | By sample testing. |  |  |
|  | Where is it monitored? | Samples are collected from the industries and tested in regional laboratory. | Who takes the action? | Regional Manager (JaEla/ Ekala) |
|  | Who monitors it? | OIC (Connection network) Ekala WRC, OIC(WRC) Ekala, Lab Assistant | When is it taken? | Immediately |
|  | When is it monitored? | Heavy metals concentration for a once a year | Who needs to be informed of the action? | AGM (GCWR), DGM(WR) |

Table 21: Operational Monitoring Plan for T1; Conveyance of Sewer through the network and Pumping Stations

| Operational monitoring plan for: Minimize the blockages and leakages in the sewer conveyance network. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Operational limits | Operational monitoring of the control measure |  | Corrective action when the operational limit is exceeded |  |
| The sewer network should be free from blockages and leaks. | What is monitored? | Percentage/length which covered the preventive maintenance in the network. | What action is to be taken? | Blockages and leakages should be repaired immediately |
|  | How is it monitored? | Visual inspections and consumer complaints |  |  |
|  | Where is it monitored? | Monthly progress meeting. | Who takes the action? | OIC(Connection network) |
|  | Who monitors it? | Regional Manager (Ja Ela/ Ekala) | When is it taken? | Immediately |
|  | When is it monitored? | Monthly | Who needs to be informed of the action? | Regional Manager (Ja Ela/ Ekala) and Engineer O&M |

Table 22: Operational Monitoring Plan for T1; Conveyance of Sewer through the network and pumping station

| Operational monitoring plan for: Encourage to wear personal protective equipment during the maintenance work. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Operational limits | Operational monitoring of the control measure |  | Corrective action when the operational limit is exceeded |  |
| All the workers should wear relevant personal protective equipment. | What is monitored? | Have PPE been provided to the workers. Do the workers wear the PPE | What action is to be taken? | Encourage the workers who wear the PPE by considering it in selecting the best worker of the month. |
|  | How is it monitored? | By visual observation. |  |  |
|  | Where is it monitored? | At the site. | Who takes the action? | OIC(Connection network) |
|  | Who monitors it? | OIC(Connection network) | When is it taken? | End of the month. |
|  | When is it monitored? | Before start the maintenance work and during the maintenance work. | Who needs to be informed of the action? | Regional Manager (Ja Ela/ Ekala) |

Table 23: Operation Monitoring Plan for T1; Conveyance of Sewer through the network and pumping station.

| Operational monitoring plan for: Avoid inhalation of toxic gases during the maintenance work. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Operational limits | Operational monitoring of the control measure |  | Corrective action when the operational limit is exceeded |  |
| The manhole/ sludge tank etc. should be free from toxic gases. | What is monitored? | Availability of the toxic Gasses | What action is to be taken? | Use the ventilator |
|  | How is it monitored? | By gas detector |  |  |
|  | Where is it monitored? | At the site. | Who takes the action? | Operator of the ventilator. |
|  | Who monitors it? | Operator of the ventilator. | When is it taken? | Before start the maintenance work. |
|  | When is it monitored? | Before start the maintenance work. | Who needs to be informed of the action? | OIC(Connection network) |

Table 24: Operational Monitoring Plan for T1; Conveyance of Sewer through the network and pumping stations.

| Operational monitoring plan for: Clean the Drainage System near the PS 02/04. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Operational limits | Operational monitoring of the control measure |  | Corrective action when the operational limit is exceeded |  |
| The drainage system should be clear to drain the water without clogging. | What is monitored? | Check the whether drained are clogged. | What action is to be taken? | Contact the Ja ela Pradeshiya saba to get clean the drains. |
|  | How is it monitored? | By visual observation. |  |  |
|  | Where is it monitored? | At the drain near the PS 02/04 | Who takes the action? | OIC(Connection network) |
|  | Who monitors it? | OIC(Connection network) | When is it taken? | When the drains are clogged at PS 02/04 |
|  | When is it monitored? | In the rainy period | Who needs to be informed of the action? | Regional Manager (Ja Ela/ Ekala) |

Table 25: Operational Monitoring Plan for T1; Conveyance of Sewer through the network and pumping station.

| Operational monitoring plan for: Check the condition/stability of the physical Structures such as manholes/pump houses/treatment plant. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Operational limits | Operational monitoring of the control measure |  | Corrective action when the operational limit is exceeded |  |
| The structures should be strong enough to be stable. | What is monitored? | Availability of corrosions, cracks, decay in the structures. | What action is to be taken? | Repair, replace, and rehabilitate the necessary parts. |
|  | How is it monitored? | By visual observation. |  |  |
|  | Where is it monitored? | Treatment plant, network, pump houses. | Who takes the action? | OIC(Connection network) |
|  | Who monitors it? | OIC(Connection network) | When is it taken? | When identify any defect |
|  | When is it monitored? | One a year | Who needs to be informed of the action? | Regional Manager (Ja Ela/ Ekala) |

Table 26: Operational Monitoring Plan for T1; Conveyance of Sewer through the network and pumping stations

| Operational monitoring plan for: well maintenance of valves in the sewer collecting network. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Operational limits | Operational monitoring of the control measure |  | Corrective action when the operational limit is exceeded |  |
| All valves should be under good working condition | What is monitored? | Functioning of the valves. | What action is to be taken? | Do repair/replace the valve according to the requirement |
|  | How is it Monitored? | Operate and checking |  |  |
|  | Where is it monitored? | In the collection network | Who takes the action? | OIC Network |
|  | Who monitors it? | OIC Network | When is it Taken? | immediately |
|  | When is it monitored? | Twice a year as per the schedule | Who needs to be informed of the action? | EA (Mechanical) & Regional Manager (Ja Ela) |

| Operational monitoring plan for: Wearing personal protective equipment during the operation. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Operational limits | Operational monitoring of the control measure |  | Corrective action when the operational limit is exceeded |  |
| Vacuum truck operators who discharge fecal sludge to Ekala water reclamation center | What is monitored? | Whether operators are wearing PPE | What action is to be taken? | Give first two instructions verbally & third instruction in writing. After the third instruction, stop the sludge disposal without PPE. |
|  | How is it monitored? | By visual observation |  |  |
|  | Where is it monitored? | At the fecal sludge unloading point of Ekala WRC | Who takes the action? | OIC (Ekala) |
|  | Who monitors it? | Engineering Assistant who approve discharge | When is it taken? | Immediately |
|  | When is it monitored? | Every time they discharge to the WRC | Who needs to be informed of the action? | Regional Manager (Ja Ela/ Ekala) |

Table 27: Operational Monitoring Plan for T1; Conveyance of FS by Vacuum Truck

Table 28: Operational Monitoring Plan for T1; Conveyance of FS by Vacuum Truck

| Operational monitoring plan for: Maintain the Quality of the fecal sludge to be discharge to the Ekala WRC. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Operational limits | Operational monitoring of the control measure |  | Corrective action when the operational limit is exceeded |  |
| Influent should be within the parameters | What is monitored? | pH, Colour, Oil and Grease | What action is to be taken? | Not Allowed to discharge fecal sludge |
|  | How is it monitored? | pH -By Testing Others – By visual observation |  |  |
|  | Where is it monitored? | At the faecal sludge unloading point of Ekala WRC | Who takes the action? | OIC (Ekala) |
|  | Who monitors it? | Engineering Assistant who approves discharge | When is it taken? | Immediately |
|  | When is it monitored? | Every time they discharge to the WRC | Who needs to be informed of the action? | Regional Manager (Ja Ela/ Ekala) |

| Operational monitoring plan for maintaining the Regular Discharge of Faecal Sludge. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Operational limits | Operational monitoring of the control measure |  | Corrective action when the operational limit is exceeded |  |
| Fecal Sludge should be regularly discharge to the Ekala WRC | What is monitored? | Continuous disposal of faecal sludge. | What action is to be taken? | Cancel the Registration for discharge the faecal sludge. |
|  | How is it monitored? | By evaluating monthly discharge reports. |  |  |
|  | Where is it monitored? | At the Manager office. By evaluating monthly discharge reports. | Who takes the action? | Regional Manager (Ja Ela/ Ekala) |
|  | Who monitors it? | Management Assistant (HR) | When is it taken? | When the faecal sludge disposal companies has not do any discharge for more than four month period. |
|  | When is it monitored? | Onece in six months | Who needs to be informed of the action? | Central Environment Authority |

Table 29: Operational Monitoring Plan for T1; Conveyance of FS by Vacuum Truck

Table 30: Operational Monitoring Plan for P4; Treatment Process at Ekala WRC

| Operational monitoring plan for: Maintain the Quality of the Influent and the effluent of the Ekala WRC. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Operational limits | Operational monitoring of the control measure |  | Corrective action when the operational limit is exceeded |  |
| Influent and effluent Parameters should be within the specified limits | What is monitored? | Water quality in inlet, Anoxic tank, Anaerobic tank and Aerobic tank. | What action is to be taken? | Review the process to identify the issue. |
|  | How is it monitored? | Sample Testing |  |  |
|  | Where is it monitored? | At laboratory of the Ekala WRC | Who takes the action? | OIC (Ekala)/Lab Assistant |
|  | Who monitors it? | Lab Assistant | When is it taken? | Immediately |
|  | When is it monitored? | Every Day | Who needs to be informed of the action? | Regional Manager (Ja Ela/ Ekala) |

Table 32: Operational Monitoring Plan for P4; Treatment Process at Ekala WRC

| Operational monitoring plan for: Maintain the Quality of the Influent and the effluent of the Ekala WRC. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Operational limits | Operational monitoring of the control measure |  | Corrective action when the operational limit is exceeded |  |
| Heavy metals should be available in sludge below the permissible levels | What is monitored? | Availability of heavy metals | What action is to be taken? | Review the process to identify the issue. |
|  | How is it monitored? | By Sample Testing |  |  |
|  | Where is it monitored? | Ambathale water treatment plant laboratory. | Who takes the action? | OIC(Ekala) |
|  | Who monitors it? | Lab Assistant | When is it taken? | When identify present of heavy metals. |
|  | When is it monitored? | Monthly | Who needs to be informed of the action? | Regional Manager (Ja Ela/ Ekala) |

Table 33: Operational Monitoring Plan for P4; Treatment Process at Ekala WRC

| Operational monitoring plan for: Maintain the Quality of the Influent and the effluent of the Ekala WRC. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Operational limits | Operational monitoring of the control measure |  | Corrective action when the operational limit is exceeded |  |
| Suspended sludge level between the 2500mg/l to 3500mg/l in the final clarifier | What is monitored? | SS Level | What action is to be taken? | Release the access sludge |
|  | How is it monitored? | From SCADA system |  |  |
|  | Where is it monitored? | At Ekala WRC | Who takes the action? | Engineering Assistant (Ekala) |
|  | Who monitors it? | Pump Operator | When is it taken? | When exceed the maximum limit |
|  | When is it monitored? | Daily | Who needs to be informed of the action? | OIC (Ekala) |

Table 31: Operational Monitoring Plan for P4; Treatment Process at Ekala WRC

| Operational monitoring plan for: Maintain the Quality of the Influent and the effluent of the Ekala WRC. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Operational limits | Operational monitoring of the control measure |  | Corrective action when the operational limit is exceeded |  |
| Dissolved Oxygen level of the aeration tank should in between 1.5mg/l and 2.0mg/l | What is monitored? | Dissolved Oxygen level of the aeration tank | What action is to be taken? | Operating the air blower correctly |
|  | How is it monitored? | From DO sensors |  |  |
|  | Where is it monitored? | Before and after the aeration | Who takes the action? | Engineering Assistant (Ekala) |
|  | Who monitors it? | SCADA System | When is it taken? | When DO level reduced |
|  | When is it monitored? | 24 hrs in 365 days online monitoring | Who needs to be informed of the action? | OIC (Ekala) |

Table 325: Operational Monitoring Plan for P4; Treatment Process at Ekala WRC

| Operational monitoring plan for: Encourage to wear personal protective equipment during the maintenance work. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Operational limits | Operational monitoring of the control measure |  | Corrective action when the operational limit is exceeded |  |
| All the workers should wear relevant personal protective equipment. | What is monitored? | Have PPE been provided to the workers. Are workers wear the PPE | What action is to be taken? | Encourage the workers who wear the PPE by considering it in selecting the best worker of the month. |
|  | How is it monitored? | By visual observation. |  |  |
|  | Where is it monitored? | At the site. | Who takes the action? | OIC(Connection network)/OIC Ekala |
|  | Who monitors it? | OIC(Connection network)/OIC Ekala | When is it taken? | End of the month. |
|  | When is it monitored? | Before start the maintenance work and during the maintenance work. | Who needs to be informed of the action? | Regional Manager (Ja Ela/ Ekala) |

Table 33: Operational Monitoring Plan for P4; Treatment Process at Ekala WRC

| Operational monitoring plan for: Avoid inhalation of toxic gases during the maintenance work. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Operational limits | Operational monitoring of the control measure |  | Corrective action when the operational limit is exceeded |  |
| The sludge tank etc should be free from toxic gases. | What is monitored? | Availability of the toxic Gasses | What action is to be taken? | Use the ventilator |
|  | How is it monitored? | By gas detector |  |  |
|  | Where is it monitored? | At the Ekala Treatment Plant | Who takes the action? | Operator of the ventilator. |
|  | Who monitors it? | Operator of the ventilator. | When is it taken? | Before start the maintenance work. |
|  | When is it monitored? | Before start the maintenance work. | Who needs to be informed of the action? | OIC(Ekala) |

Table 34: Operational Monitoring Plan for P4; Treatment Process at Ekala WRC

| Operational monitoring plan for: Check the condition/stability of the physical Structures such as manholes/pump houses/treatment plant. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Operational limits | Operational monitoring of the control measure |  | Corrective action when the operational limit is exceeded |  |
| The structures should be strong enough to be stable. | What is monitored? | Availability of corrosions, cracks, decay the structures. | What action is to be taken? | Repair, replace, and rehabilitate the necessary parts. |
|  | How is it monitored? | By visual observation. |  |  |
|  | Where is it monitored? | Treatment plant | Who takes the action? | OIC(Ekala) |
|  | Who monitors it? | OIC(Ekala) | When is it taken? | When identify any defect |
|  | When is it monitored? | One a year | Who needs to be informed of the action? | Regional Manager (Ja Ela/ Ekala) |

Table 38: Operational Monitoring Plan for P6; Discharge of Effluent

| Operational monitoring plan for: Maintain the quality of effluent to the Dandugam Oya |  |  |  |  |
| --- | --- | --- | --- | --- |
| Operational limits | Operational monitoring of the control measure |  | Corrective action when the operational limit is exceeded |  |
| The effluent after the wastewater treatment should be consistence with the Gazette No 2264/17, 2022 requirements | What is Monitored? | Ph, Temperature, DO, TSS, Color, BOD, COD, TDS, RCL of the final clarifier. | What action is to be taken? | Review the process to identify the issue |
|  | How is it Monitored? | By sample testing |  |  |
|  | Where is it monitored? | At the Ekala water reclamation center | Who takes the action? | OIC (Ekala) / Lab Assistant) |
|  | Who monitors it? | Lab assistant | When is it taken? | When tested parameters are out of the standards |
|  | When is it monitored? | Once a week | Who needs to be informed of the action? | Regional Manager (Ja Ela/ Ekala) |

## 5.2 Verification of System Performance

Table 39: Verification of System Performance

| Sanitation Step | Verification |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | What | Limit | When | Who | Method |
| T1: Conveyance of Sewer through the network and pumping stations. | The time taken to attend a blockage/leak | < 48 hours | Monthly | Regional Manager (Ekala/Ja Ela) | Monthly progress report & monthly progress meeting. |
| T1: Conveyance of Sewer through the network and pumping Stations. | % of No. of complaints attended within 48 hours. | > 98% | Monthly | Regional Manager (Ekala/Ja Ela) | Monthly report & monthly progress meeting |
| T2: Conveyance of FS by vacuum trucks | pH Value, Color, Odor and Oil | Ph – 6-8 Colour Odor - acceptable level according to the visual observation Oil – Not Allowed | Before discharge | Pump Operator | Field testing & Visual observations |
| P4: Treatment Process | BOD, COD, TSS, Colour Level in the influent, and the effluent of the treatment plant. | COD <250mg/l BOD < 30mg/l TSS < 50 mg/l | Once a week | Lab Assistant | By sample testing |
| Entire treatment process | Environmental protection license | One year | Annually | Central Environment Authority | By inspection and sample testing. |

## 5.3 Auditing the System

It was decided to review and audit the sanitation safety planning of Ekala WRC internally once in a year and externally once in a year.

# DEVELOPMENT OF SUPPORTING PROGRAMMES AND REVIEW PLANS

## 6.1 Identification and Implementation of Supporting Programmes

- Involve Ja-Ela Pradeshiya Sabha in cleaning the drainage system near Pump House 02 (PS 02).
PS 02 is prone to flooding during heavy rains, particularly during the southwest monsoon from May to June, and storm water becomes contaminated with wastewater. It is crucial to maintain a proper drainage system in the PS 02 area to minimize flooding during the rainy season. The drainage system is outside the control of the NWSDB, so the involvement of Ja-Ela Pradeshiya Sabha is necessary to ensure the drainage system is maintained without blockages. A support program from the Ja-Ela Pradeshiya Sabha is essential. A stakeholder meeting should be held, and a memorandum of understanding should be established to clean the drainage system periodically.

- Involve the Disaster Management Center to find a suitable solution to prevent flooding near the PS 02 area.
Although efforts have been made to clean the drains near PS 02, flooding still occurs during heavy rain. Therefore, further assistance is needed to manage the situation. The Disaster Management Center is aware of this issue, and their support is required to find a long-term solution to prevent flooding in the area.

- Organize an awareness program for potential entrepreneurs about the possibility of using dried sludge to produce organic fertilizers (compost).

Disposing of dried sludge from the wastewater treatment process is a significant problem, and during the rainy season, storm water can contaminate the dried sludge. By organizing an awareness program to highlight the potential use of dried sludge for making organic fertilizers, new opportunities for sludge disposal can be created.

- Supportive Programs to avoid the entry of heavy metals, oil, grease, rainwater, etc., into the wastewater treatment process.
The Ekala Water Reclamation Center operates a biological treatment process, which can be disrupted by unsuitable inflows such as heavy metals, dyes, and rainwater. Although this has not yet become a serious problem, it may interfere with the biological treatment process in the future. Additionally, heavy metals are not treated by the biological process and may be released with the dried sludge. To reduce the impact of heavy metals on the Ekala Water Reclamation Center, awareness programs should be organized with commercial organizations in the Ekala Industrial Zone.

- Program to enhance coverage with vacuum pump service providers.
The Sanitation Safety Plan (SSP) targets the Ekala Wastewater Treatment Plant to enhance the coverage with vacuum truck services and to increase the number of registered vacuum truck service providers who discharge fecal sludge at the facility. By conducting programs in collaboration with the Environmental Police, it will be possible to increase the number of private vacuum truck service providers using the Ekala Wastewater Treatment Plant. This will ensure safe sewage disposal in the areas surrounding Ekala by providing a secure end-use option.

- Map the locations of leak points/overflows on the network map.
By mapping the leak and overflow points on the network using GPS coordinates, it will be easier to identify the most vulnerable areas in the collection network. This will help prioritize areas requiring special attention for maintenance work, improving smooth conveyance throughout the network.

- Environmental Authority for dispose the grit removal/screening to the sanitary landfilling.

Actions have taken and to discharge screenings to sanitary landfilling at Dompe with the successive collaboration with CEA

## 6.2 Periodic Reviewing and Updating the SSP Outputs

The SSP team decided to revise the SSP in 12 months with the members of the steering committee.