Sanitation Safety Planning

National Water Supply and Drainage Board

Seethawaka Export Processing Zone

Avissawella

Authors:

Positions:

Date:

Place:

MODULE 1

1: PREPARING FOR SANITATION SAFETY PLANNING

STEP 1.1: Define the SSP area and lead organization

What is the name of the locality in which SSP will be developed?

National Water Supply & Drainage Board Water Reclamation Division - Manager Office (Seethawaka)

In the following lines, describe the locality.

- Where it is located. Mention in which part of the country is located, the governance structure in the country (units could be states, provinces, regions, etc.) and indicate to which units the locality belongs to. Indicate the area covered (in km2).

Water Reclamation Division - Manager Office(Seethawaka) is located in Avissawella, Western Province of Sri lanka. The sewer network of SEPZ covers around 430 Acres of the SEPZ parameters.Water treatment plant (WTP) which has a capacity of 9950m3/day is operated by extracting raw water from the “Kelani River”. Then the distributed portable water is consumed by the factories in the SEPZ and industrial wastewater is generated by them.The main focus of the Sanitation Safety Planning (SSP) is the aforementioned CWWTP and it is operated & maintained by the Manager Office (Seethawaka) of the National Water Supply & Drainage Board (NWSDB) but the overall legal proprietorship of all the assets in WTP and CWWTP belongs to the Board of Investments (BOI) - Sri Lanka.

- Number of inhabitants, the number of households, average of people per household, literacy rate and any key information about division of ethnic groups, socio-economic stratification, and vulnerable communities.

Seethawaka Export Processing Zone (SEPZ) was established in 1999 and currently there are about 26 number of different industries under commercial operation. Garments, washing, rubber, food, chemicals are some of the major industries in the SEPZ and about 27000 employees are working here. The industrial categorization of the SEPZ is shown in figure…………………..

- Main sources of household revenues and average income, describe also if there is any agriculture activity in the region and type of crops.

The industrial wastewater and the sewerage from the factory toilets were collected and transported to a common wastewater treatment plant (CWWTP) which has a capacity of 9900m3/day, through gravity pipe lines.The wastewater from 27,000 workers who are working in the SEPZ is accommodated as long as their waste is domestic in nature, whereas the 26 factory effluents are in industrial nature.

- Monthly average temperature, precipitation (in mm) and seasonality (e.g. dry and rainy season).

- Indicate clearly what type of climate change scenario is projected for the near future.

- Prevalence of excreta-related diseases observed in the community (cholera, diarrhea, dysentery, hepatitis A, typhoid, polio, parasitic worms, etc.).

Fecial- related diseases have not been specifically observed.

- Main water source and characteristics of the water supply.

Water treatment plant (WTP) which has a capacity of 9,950m3/day is operated by extracting raw water from the “Kelani River”. Then the distributed portable water is consumed by the factories in the SEPZ and industrial wastewater is generated by them.

Which lead organization will run the entire SSP process?

The main focus of the Sanitation Safety Planning (SSP) is the aforementioned CWWTP and it is operated & maintained by the Manager Office (Seethawaka) of the National Water Supply & Drainage Board (NWSDB) but the overall legal proprietorship of all the assets in WTP and CWWTP belongs to the Board of Investments (BOI) - Sri Lanka. All exposed groups and the associated health-risks will also be identified within the identified boundary. Table 1.1 lists the components and activities that define the SSP boundary. Table 1.1: List of Activities Included in the SSP boundary Components/Activities; Lead Organization. Generation of industrial waste & sewage; SSP Team (Factories). Collection of industrial waste & sewage through the sewer lines, operation and maintenance of sewer network & CWWTP, treatment of wastewater at the CWWTP.; SSP Team (NWSDB). Safe sludge disposal & storm water outfall management; SSP Team (BOI).

STEP 1.2: Assemble the SSP team

Which person will be the SSP team leader?

Remember that the team leader should have the authority, the organizational and interpersonal skills, and sufficient time and management resources to ensure that the process can be implemented effectively.

Eng. M.B.M. Thilakarathne the Manager of Seethawaka will lead the SSP Team.

Which person/organization will be part of the SSP team?

The usual process is to: (1) do a stakeholder analysis and (2) select team membership to suit the SSP purpose. Limit the number of team members to keep the working group functional.

| Organization | Job title | Role in SSP team |
| --- | --- | --- |
| Factory wise Ms. Teejay Lanka Pvt Ltd. Eng. Edge Melon Ms. Lalan Rubber Pvt Ltd. Mr. Bandula(Factory Manager) Ms. Hydramani Factory Manager Ms.Bishoff Gamma Eng. M.Samarakoon(Head Of Engineering) | Wastewater generation | Communicate the internal sanitation issues |
| Water Board Eng. W.M.A.B. Thilakarathne Mr. Sumith Mr. Rajapakshe Mr. Pushpakumara Mr. Kosala Mr. Dinith Mr. Isuru Mr. Abeyrathne Mrs. Nirosha | Operations & Maintenance Resident Manager Plant Operator plant Operator Dehydrator Operator Technician Workshop Assistant Labourer lab Assistant Lab Attendant | Provide information on existing sanitation issues. Provide information on existing sanitation issues. Provide technical support. Provide technical support. Provide technical support. Identify and inform loopholes. Monitoring and verification process. Monitoring and verification process. |
| Board Of Investment Mr. Sujeewa Thilakumara Ms. Lasitha Athauda Mr. Susantha | Director (SEPZ) Environmental Officer Tractor Driver | Safe disposal of the dehydrated sludge. Provide guidance for environmental protection. Provide information about the issues in the sludge transportation process. |
| District General Hospital(Avissawella) Dr. Udani Saparamadu CEA | Public Health MO Provide guidance for the environmental protection | Public wellbeing assessment. Investigate about the public health hazards and facilitate any required resources. |
| PHI | Provide guidance for the environmental protection | Investigate about the public health hazards and facilitate any required resources |

MODULE 2: DESCRIBE THE SANITATION SYSTEM

Prepare a sanitation map that includes all steps of the sanitation system: toilet, containment-storage/ conveyance/emptying/transport, treatment and disposal/reuse). Paste the map here.

Sewerage Network

The system starts with factories where wastewater is generated. At present around 26 factories are connected to the sewer network which lies around 4.5 km across Seethawaka Export Processing Zone (SEPZ) boundary. These sewer lines enable the conveyance of wastewater to the central wastewater treatment plant. The wastewater from 27,000 workers who are working in the SEPZ is accommodated as long as their waste is domestic in nature, whereas the 26 factory effluents are in industrial nature. The sewer network of SEPZ covers around 430 Acres of the SEPZ parameters.

Water Reclamation Centre

In areas where sewer lines are available, industrial establishments and office units can be connected to the nearest sewer line.

Water reclamation center SEPZ is a combination of a preliminary, secondary and tertiary treatment process.

The water reclamation center of SEPZ treats wastewater from the free trade zone of Seethawaka. The wastewater treatment plant at the SEPZ uses conventional methods to remove pollutants from the wastewater. These technologies include physical, chemical and biological processes. The treated wastewater is then discharged into the Kelani river. The water reclamation centre of SEPZ has a capacity 10,000 m3/day.

STEP 2.2: Characterize system flows

Use the following table to characterize system flows (for instance, feces, urine, excreta, wastewater, greywater, sludge collected, sludge emptied, dried feces, solid waste dumped in the pit etc.) Read guidance note 2.2 and tool 2.1 for more information. Include all the quantitative information you have and identify if the system flow might have a biological, chemical or/and physical hazards.

| System flow code | Sanitation step | Description of the system flow | Key information of the system flow | Expected variations | Type of potential hazard |
| --- | --- | --- | --- | --- | --- |
|  | IC |  |  |  |  |
|  | Manhole |  |  |  |  |
|  | Sewer Line |  |  |  |  |
|  | Grit Chamber | Separating grit from wastewater |  |  | Odor related issued. Contact with solid waste and pathogens/ helminth eggs in maintenance and grit removing process. |
|  | Coarse Screen | Removing large/medium scale floating waste |  |  | Contact wastewater, solid waste and pathogens/helminth eggs in maintenance process and transporting process to storage area. Open for animals when open dumping. |
|  | Fine Screen | Removing small scale floating waste |  |  | Contact wastewater, solid waste and pathogens/helminth eggs in maintenance process and transporting process to storage area. Open for animals when open dumping. Contact wastewater, solid waste and pathogens/helminth eggs due to |
|  | Balancing tank | Regulating and mixing the flow |  |  | Contact with pathogens/ helminth eggs when inspecting repairing and maintaining. Odor related issues. |
|  | Oxidation Ditches | Supplying Oxygen for influent |  |  | Inhaling aerosol due to aeration. Contact with pathogens / helminth eggs when repairing and maintaining – very rare. |
|  | Final Settling Tank | Removing formed flocks and scum |  |  | Maintenance/ Emptying – Contact with pathogens/helminth eggs. Falling potential. Potential physical damage when working with scraper machine. Daily cleaning- Contact with pathogens/ helminth eggs from effluent of sedimentation tank. Some amount of flock and TSS are scaping to disinfection tank. |
|  | Chlorine Storage |  |  |  | Instruction has given |
|  | Chlorine mixing pipe line | Mixing chlorine to the water for disinfection purposes. |  |  | Effluent from disinfection tank is using. Inhale harmful gases due to chemical reactions. |
|  | Sludge Thickener Tank | Storing sludge from a sedimentation tank to use for dewatering. |  |  | Contact with pathogens/ helminith eggs maintenance. Animals can enter due to improper covering. |
|  | Dewatering Process (belt press machine) | Removing excess water from sludge. |  |  | Effulent from disinfection tank in using. Contact Polymer. Electric controllers and workers/ visitors are in a wet environment. Workers don’t use any safety equipment such as masks, gloves etc.when working with polymer. Water use from disinfection tank and that water can spill to bodies. There is a possibility to skip the belt near the water and electricity. |
|  | Storing dewatered sludge at plant before transporting (After belt press machine) | for further processing |  |  |  |
|  | Transporting dewatered sludge | land filling |  |  | Spilling along the road. contact with sludge when loading and unloading sludge. |
|  | Chemical Storage Tank | Storing Chemicals |  |  | expose to chemicals. Accidents due to explosions etc.. |
|  | Gardening inside the plant |  |  |  | Contact with effluent of disinfection tank and sludge while gardening. Consuming vegetables and fruits from the garden. |

STEP 2.3: Identify exposure groups

In your maps, identify the exposure groups, using the letters U, L, W, WC, F and C are as symbols. You might want to define sub-groups, such as U1: users of latrines, U2: users of flush toilets. Use SSP manual Tool 2.2 on page 32 to characterize the exposure groups. Remember the exposure groups are:

U: Sanitation system users				L: Local community				W: Sanitation workers

WC: Wider community					F: Farmers 					C: Consumers:

| Sanitation step | Exposure Group ID | Who are the exposure groups? | How many are there? | What are they doing there? | What are they exposed to? | How often are they exposed to this? |
| --- | --- | --- | --- | --- | --- | --- |

STEP 2.4: Gather supporting information

Write down any information you will want to obtain to characterize the system. Indicate the source of the information. Record below:

| Regulatory requirements | Demographics and land use patterns |
| --- | --- |
| System management and performance | Changes related to climate and weather |

MODULE 3: IDENTIFY HAZARDOUS EVENTS, AND ASSESS EXISTING CONTROL MEASURES AND EXPOSURE RISKS

Overview

Specifying each step in the system is essential in determining potential hazards and hazardous exposure events for the exposure groups. This leads to the assessment of the risks and the extent at which these are controlled. The result of this step in the SSP is to ensure that subsequent efforts and investments on the system monitoring and improvements respond to actual rather than perceived health risks.

STEP 3.1: Identify hazards and hazardous events

The hazards and hazardous exposure events are identified for the different processes in the system. Table 3.1 shows these identified hazards and hazardous exposure events. This helps in identifying who may be placed at risk and how the exposure risk occurs. The columns (02) and (03) represent the hazardous events and the hazards which are exposed in each sanitation step.

When applying step 3.1, only complete the columns Component and Hazard identification. Make sure you describe the Hazardous event telling the story of how the hazards cause harm, including the exposure route (ingestion after contact with excreta, ingestion of contaminated water, consumption of contaminated produce, dermal contact, vector-borne, inhalation). Revise the Newtown worked case study, the example 3.2 and guidance note 3.4 for examples).

STEP 3.2: Refine exposure groups and exposure routes

Identified hazard and hazardous exposure events must be related to its corresponding exposure groups and the routes by which these groups may be affected. Below is the list of exposure groups and its corresponding code. The column (04) represents the exposure groups of the hazardous events and the hazards which are defined in step 3.1.

When applying step 3.2, only complete the columns related to Existing Controls. Remember that “Validation of control(s)” refers to the method how you are able to verify if the existing control is working or not. For example, field visits, interviews, tests, revision of reports, etc.

STEP 3.3: Identification and Assessment of Existing Control Measures

For each of the hazard exposure events identified in Table 3.1, Septage and Sewage treatment identified existing control measures to mitigate the risk of such hazardous exposure events. The said control measures were then assessed on their affectivity in reducing the risk of the exposure event. The columns (06) and (07) represent the existing control measures and their effectiveness.

The risks were assessed based on its likelihood and severity as shown on Table 3.2. The computed level of risk and likelihood equates to the ranking of risks as shown in Table 3.3 wherein the risk level was identified. Furthermore, the risk category is described in Table 3.4 to highlight the actions to be taken upon assessing the risk

STEP 3.4: Assess and prioritize the exposure risk

Due to the large number of identified hazards and hazard exposure events in the previous section, not all of them will be addressed immediately due to limited resources available. The team evaluated the risk rating of each before considering those that need an immediate action plan and those that can be planned in the future. Most of the items prioritized by the team are those with high-risk ratings.

When applying step 3.3, complete the columns related to the risk assessment. Use tools 3.5 and 3.6 of your SSP manual (page 58) for definitions and scores of likelihood, severity and risks. Decide two most likely climate change scenarios and decide with your team if the risk will increase, decrease or will remain the same. Make sure you write in the comments box, the reasons that justify your choice.

| Component | Hazard Identification |  |  |  | Existing Control(s) |  |  | Risk Assessment (08) |  |  |  |  |  | Comments justifying risk assessment, under current conditions or climate change scenarios, or effectiveness of the control |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | Under current conditions |  |  |  | Under the most likely climate change scenarios: + means increased risk - means decreased risk = means the same risk |  |  |
|  |  |  |  |  |  |  |  | L=Likelihood; S=Severity; R=Risk |  |  |  |  |  |  |
| Sanitation step (01) | Hazardous event (02) | Hazard (03) | Exposure Groups (04) | Number of persons at risk (05) | Description of existing control (06) |  | Validation of control (07) | L | S | Score | R | R/F | Drought |  |
| Conveyance | Ingestion of pathogens after contact with excreta due to overflowing of IC due to blockage solid waste | Biological | Staff of the factory, Maintenance personnel | 5,000 | - |  | Visual inspection shows | 4 | 2 | 8 | M | + | - |  |
| Conveyance | Dermal contact with pathogens after contact with raw sewer due to the overflowing of sewer manholes | Biological | General Public, Maintenance personal | 30,000 | Usage of PPE |  | Visual inspection shows O&M personnel usually not using | 4 | 2 | 8 | M |  |  |  |
| Conveyance | Ingestion of pathogens Mixing the raw sewer with the water source due to the overflowing of a manhole | Biological | General public | 1000,000 | - |  | - | 3 | 4 | 12 | M |  |  |  |
| Conveyance | Trauma or asphyxiation caused when opening manhole to remove blockage | Chemical | Sewer Network Maintenance Personnel | 03 | PPE & safety instructions |  | Visual inspection | 5 | 2 | 10 | M | = | = |  |
| Conveyance | Ingestion of pathogens after contact with excreta during the removing of the blockage | Biological | Sewer Network Maintenance Personnel | 03 | PPE & safety instructions |  | Visual inspection |  |  |  |  |  |  |  |
| Conveyance | Physical damage fell down into a manhole due to the unavailability of a manhole cover or defective cover. | Physical | Sewer Network Maintenance Personnel/ General Public | 30,000 | - |  | - | 1 | 8 | 8 | M | + | = |  |
| Conveyance | Dermal contact with pathogens after contact with raw sewer Fallen down into a manhole due to the unavailability of a manhole cover or defective cover. | Biological | General Public | 30,000 | - |  | - | 2 | 8 | 16 | H | + | = |  |
| Conveyance | Dermal contact with pathogens after contact with raw sewer while repairing a damaged sewer line. | Biological | Sewer Network Maintenance Personnel | 3 | PPE & safety instructions |  | Visual inspection |  |  |  |  |  |  |  |
| Conveyance | ingestion of pathogens after contact with waste water while repairing a damaged sewer line. | Biological | Sewer Network Maintenance Personnel | 3 | PPE & safety instructions |  | Visual inspection |  |  |  |  |  |  |  |
| Conveyance | Trauma or asphyxiation caused while repairing a damaged sewer line. | Chemical | Sewer Network Maintenance Personnel | 3 | PPE & safety instructions |  | - |  |  |  |  |  |  |  |
| Conveyance | Physical damage Fallen down into a manhole when repairing leak due to corrosion ladder | Physical | Sewer Network Maintenance Personnel | 3 | safety instructions |  | Visual inspection |  |  |  |  |  |  |  |
| Conveyance | physical damaged because of electrocution while leak repairing due to leakage of eclectic cable | Physical | Sewer Network Maintenance Personnel | 3 | safety instructions |  | Visual inspection |  |  |  |  |  |  |  |
| Conveyance | physical damage due to the collapse of excavated trenches when repairing a damaged sewer line. | Physical | Sewer Network Maintenance Personnel | 3 | safety instructions |  | Visual inspection |  |  |  |  |  |  |  |
| Conveyance | physical damage by hitting a equipment when repairing a damaged sewer line. | Physical | Sewer Network Maintenance Personnel & General public | 30,000 | safety instructions |  | Visual inspection |  |  |  |  |  |  |  |
| Conveyance | physical damage due to vehicles falling on the road which is not properly refilled of leak repair area of the road. | physical | General Public | 30,000 |  |  |  |  |  |  |  |  |  |  |
| Treatment | Exposure to the raw sewer due to overflowing of the Grit Chamber because of clogging of course/ fine screens | Biological, Chemical | WWTP Operation & Maintenance Personnel | 10 | Usage of PPE |  | Visual inspection shows O&M personnel usually not using | 4 | 2 | 8 | M | + | = |  |
|  |  | Physical |  | 10 |  |  |  | 1 | 5 | 5 | L | + | = |  |
| Treatment | Exposure to the raw sewer during the grit cleaning works | Biological, Chemical, Physical | WWTP Operation & Maintenance Personnel | 10 | Usage of PPE |  | Insufficient | 4 | 2 | 8 | M | = | = |  |
| Treatment | Exposure to the solid waste during the fine screen cleaning | Biological, Chemical, Physical | WWTP Operation & Maintenance Personnel | 4 | Usage of PPE |  | Visual inspection shows O&M personnel usually not using | 5 | 1 | 5 | L | = | = |  |
| Treatment | Mosquito breeding due to open disposal of solid waste from the screens | Biological | WWTP Operation & Maintenance Personnel / General public | 25,000 | Open fire |  | Visual observations | 4 | 8 | 32 | H | + | - |  |
| Treatment | Exposure to the untreated grit removed from the Grit Chamber | Biological | General public | 25,000 |  |  |  |  |  |  |  |  |  |  |
|  |  | Chemical |  |  |  |  |  |  |  |  |  |  |  |  |
| Treatment | Ingestion of pathogens after infiltration of wastewater to the groundwater due to improperly repairing of wastewater pipeline | Biological | General Public | 1,000,000 | - | - |  | 4 | 2 | 8 | M |  |  |  |
| Treatment | Dermal contact with wastewater due to overflowing of the Equalization tank in a rainy day | Biological | WWTP Operation & Maintenance Personnel / BOI Staff/ Visitors | 50 | Safety instructions | - |  | 4 | 2 | 8 | M | + | - | Munasinghe |
| Treatment | Truma or asphyxiation caused when opening the manhole covering plates to check the level of the Eq. tank | Chemical | WWTP Operation & Maintenance Personnel | 10 | PPE |  |  | 5 | 3 | 15 | H | = | = |  |
| Treatment | Ingestion of wastewater due to falling into the Eq. tank while opening the manhole covers for check the level of wastewater | Biological | WWTP Operation & maintenance Personnel | 10 |  |  |  | 2 | 16 | 32 | H | + | - |  |
| Treatment | Physical injured due to falling in to the EQ tank while walking for inspection on the EQ tank | Physical | WWTP Operation & Maintenance Personnel / BOI Staff | 15 |  |  |  | 1 | 16 | 16 | H | + | - |  |
| Treatment | Truma or asphyxiation caused due to leakage of poisoning gasses from less tightly connecting joints of exhaust pipe line | Chemical | WWTP Operation & Maintenance Personnel / BOI Staff/ Visitors | 50 |  |  |  | 1 | 8 | 8 | M |  |  |  |
| Treatment | Dermal exposure to wastewater when leak repair works of No. 2 lift pump | Biological | WWTP Operation & Maintenance Personnel | 10 |  |  |  | 1 | 8 | 8 | M |  |  |  |
| Treatment | Physical damage due to Lightning shock while walking on the EQ tank to check the level of wastewater | Physical | WWTP Operation & Maintenance Personnel | 10 | - | - |  | 1 | 16 | 16 | H | ++ | - |  |
| Treatment | Physical damaged by electrocution due to leakage of the electric cable on the EQ | Physical | WWTP Operation & Maintenance Personnel / BOI Staff/ Visitors | 50 |  |  |  |  |  |  |  |  |  |  |
| Treatment | Physical damaged due to blasting of Blower line due to aged pipe line & blockage of nozzles | Physical | WWTP Operation & Maintenance Personnel / BOI Staff/ Visitors | 50 |  |  |  |  |  |  |  |  |  |  |
| Treatment | Physical damaged due to falling down from EQ tank | Physical | WWTP Operation & Maintenance Personnel / BOI Staff/ Visitors | 50 |  |  |  |  |  |  |  |  |  |  |
| Treatment | Ingestion of contaminated water with raw sewage due to bypassing of wastewater treatment plant | Biological | General Public | 5,000,000 | - | Visual Observation |  |  |  |  |  |  |  | Indika |
| Treatment | Dermal contact with high PH wastewater from industries | Chemical | WWTP Operation & Maintenance Personnel / | 10 | PPE | Test results |  | 3 |  |  |  |  |  |  |
| Treatment | Physical damage due to falling down of the temporary pumping line from Eq.tank to OD’s due to decay of wooden supports. | Physical | WWTP Operation & Maintenance Personnel / Visitors | 10 | Temporary supports | Visual observations |  | 2 | 4 | 8 | M | = | = |  |
| Treatment | Injection of wastewater due to out of service the plant by falling down of the temporary pumping line from Eq.tank to OD’s due to decay of wooden supports. | Biological | WWTP Operation & Maintenance Personnel / Visitors | 50 | _ | _ |  | 2 | 2 | 4 | L | = | = |  |
| Treatment | Dermal contact with wastewater due to falling down of the temporary pumping line from Eq.tank to OD’s due to decay of wooden supports. | Biological | WWTP Operation & Maintenance Personnel / Visitors | 50 | - | - |  | 2 | 2 | 4 | L | = | = |  |
| Treatment | Physical injury due to Slip of legs while climbing the stairs of WWTP | Physical | WWTP Operation & Maintenance Personnel / Visitors | 50 | Hand rail |  |  | 2 | 8 | 16 | H | + | _ |  |
| Treatment | Inhalation of particles and aerosol containing pathogens near the OD canal at the point of inlet when inspection the OD’s | Chemical | WWTP Operation & Maintenance Personnel | 10 |  | _ |  | 4 | 2 | 8 | M | = | = |  |
| Treatment | Physical injury due to the part of the aerator break into pieces and hit on a personal while inspecting the OD’s | Physical | WWTP Operation & Maintenance Personnel / Visitors | 50 |  |  |  | 2 | 4 | 8 | M | = | = |  |
| Treatment | Ingestion of wastewater due to Collapse of a plate on the canal of delivering raw sewer to the ditches while doing the operational works | Biological | WWTP Operation & Maintenance Personnel | 10 | - | Visual Observation |  | 2 | 4 | 8 | M | = | = |  |
| Treatment | Dermal exposure to wastewater when operate the valve due to Collapse of a plate on the canal of delivering raw sewer to the ditches | Biological | WWTP Operation & Maintenance Personnel | 10 |  |  |  | 2 | 2 | 4 | L | = | = |  |
| Treatment | Physical injury due to Collapse of a plate on the canal of delivering raw sewer to the ditches | Physical | WWTP Operation & Maintenance Personnel | 10 |  |  |  | 2 | 8 | 16 | H | = | = |  |
| Treatment | Physical injury of accident due to hitting spare parts removed for maintenance purposes | Physical | WWTP Operation & Maintenance Personnel / Visitors | 50 | - | Visual Observation |  | 2 | 2 | 4 | L | + | - |  |
| Treatment | physical damaged because of electrocution while checking the instruments due to electrical leakage in a motor of WWTP | Physical | WWTP Operation & maintenance Personnel | 10 |  | Visual observation |  | 2 | 8 | 16 | H | + | - |  |
| Treatment | Physical damaged due to blasting a electrical panel of WWTP | Physical | WWTP Operation & Maintenance Personnel / Visitors | 50 | - | - |  | 1 | 16 | 16 | H | + | - |  |
| Treatment | Ingestion of pathogens after contact with wastewater due to Collapse a iron plate cover of the aerator rotary wheel OD’s | Biological | WWTP Operational & maintenance Personnel | 10 |  |  |  | 3 | 4 | 12 | M | = | = |  |
| Treatment | Physical damaged due to Collapse a iron plate cover of the aerator rotary wheel OD’s | Physical | WWTP Operational & maintenance Personnel | 10 |  |  |  | 3 | 8 | 24 | H | = | = |  |
| Treatment | Dermal contact with pathogens by contact with wastewater due to collapse a iron plate cover of the aerator rotary wheel OD’s | Biological | WWTP Operational & Maintenance Personnel | 10 |  |  |  | 3 | 2 | 6 | M | = | = |  |
| Treatment | Physical damaged due electrocution when operate a switch of panel boards in WWTP | Physical | WWTP Operational & Maintenance Personnel | 10 |  |  |  | 1 | 8 | 8 | M | - | - |  |
| Treatment | Physical damaged by accident due to mistaken operation of an electrical switch in WWTP, that is closed during maintenance work | Physical | WWTP Operational & Maintenance Personnel | 10 |  |  |  | 4 | 16 | 64 | VH | = | = |  |
| Treatment | Ingestion of pathogens after contact with wastewater because of a accident due to mistaken operation of an electrical switch that is closed during maintenance work | Biological | WWTP Operational & Maintenance Personnel | 10 |  |  |  | 4 | 8 | 32 | H | = | = |  |
| Treatment | Physical damaged due to Being struck by lightning on a slab tops in WWTP | Physical | WWTP Operation & Maintenance Personnel / Visitors | 50 |  |  |  | 2 | 16 | 32 | H | + | - |  |
| Treatment | Physical damaged by electrocution due to leakage of a power cables in WWTP | Physical | WWTP Operation & Maintenance Personnel / Visitors | 50 |  |  |  | 1 | 16 | 16 | H | + | - |  |
| Treatment | Ingestion of pathogens after contact with raw wastewater due to fall down to a ditch when operate the valves of the raw sewer delivering canal | Biological | WWTP Maintenance Personnel | 10 |  |  |  | 2 | 8 | 16 | H | + | - |  |
| Treatment | Ingestion of pathogens after contact with activated sludge When operate return sludge valves | Biological | WWTP Maintenance Personnel | 10 |  |  |  | 3 | 2 | 6 | M | + | - |  |
| Treatment | Dermal contact with pathogens due to contact with activated sludge when operate the return sludge valves | Biological | WWTP Maintenance Personnel | 10 |  |  |  | 3 | 2 | 6 | M | + | - |  |
| Treatment | Dermal contact with pathogens by exposure to the activated sludge when maintenance work of excess sludge temporary storage box | Biological | WWTP Maintenance Personnel | 10 |  |  |  | 3 | 2 | 6 | M | + | - |  |
| Treatment | Dermal contact with pathogens by exposure to the activated sludge when transferring excess sludge through the ditches | Biological | WWTP Maintenance Personnel | 10 |  |  |  | 3 | 2 | 6 | M | + | - |  |
| Treatment | Ingestion of pathogens after contact with partly treated wastewater due to slips of legs when cleaning a final settling tank | Biological | WWTP Maintenance Personnel | 10 |  |  |  | 2 | 4 | 8 | M | + | - |  |
| Treatment | Physical damaged due to slips of legs when cleaning a final settling tank | Physical | WWTP Maintenance Personnel | 10 |  |  |  | 2 | 8 | 16 | H | + | - |  |
| Treatment | Ingestion of pathogens after contact with partly treated wastewater by slipping of legs and fall down to the point of chlorine dosing of final settling tank A | Biological | WWTP Maintenance Personnel | 10 |  |  |  | 2 | 4 | 8 | M | + | - |  |
| Treatment | Dermal contact with high chlorine concentration treated water when cleaning the trenches due to malfunction of chlorine dosing pump. | Chemical |  |  |  |  |  |  |  |  |  |  |  |  |
| Treatment | Physical damaged by slipping of legs & fall down to the point of chlorine dosing of final settling tank -A | Physical | WWTP Maintenance Personnel | 10 |  |  |  | 2 | 16 | 32 | H | + | - |  |
| Treatment | Dermal contact due to an explosion of a chlorine tank when refilling / lifting | Chemical | WWTP Maintenance Personnel | 10 |  |  |  | 2 | 16 | 32 | H | + | - |  |
| Treatment | Dermal contact with the raw wastewater when obtaining samples in the WWTP | Biological | WWTP operation & maintenance personnel and laboratory staff | 06 | PPE | Visual observation |  | 3 | 2 | 6 | L | = | = | Gayani |
| Treatment |  | Chemical (Heavy Metal Effect) |  | 06 | PPE & safety instructions | Visual observation |  | 3 | 16 | 48 | VH | = | = |  |
| Treatment | Physical damage due to Slip of legs while sampling at the OD’s | Physical | WWTP operation & maintenance personnel & laboratory staff | 06 | Handrails | Visual observation |  | 2 | 16 | 32 | VH | + | - |  |
| Treatment | Ingestion of pathogens after contact with wastewater due to Slip of legs while sampling at the OD’s | Biological | WWTP operation & maintenance personnel & laboratory staff | 06 | Handrails | Visual observation |  | 2 | 8 | 16 | H | + | - |  |
| Treatment | Trauma or asphyxiation caused by exposuring to toxic gasses and chemicals when conducting the analysis in the lab. | Chemical | Personnel, visitors and laboratory staff | 50 | PPE& Handle the toxic chemicals in a fume hood. | Visual observation |  | 2 | 8 | 16 | H | = | = |  |
| Treatment | Physical harm from the explosion, caused by using unsafe glassware for the heating purpose, while conducting the analysis in the lab. | Physical | Laboratory Staff | 03. | Usage of heat adaptive glassware (Eg. Borosilicate, Pyrex materials | Visual Observation |  | 2 | 8 | 16 | H | = | = |  |
| Treatment | Dermal contact with the toxic chemicals and the concentrated acids when conducting the analysis in the lab | Physical | Laboratory staff | 03 | 1.Usage of PPE 2.Handle chemicals in a fume hood. | Visual Observations. |  | 2 | 16 | 32 | H | =] | = |  |
|  |  | Chemical |  |  |  |  |  | 2 | 16 | 32 | H | = | = |  |
|  |  | Biological |  |  |  |  |  | 3 | 2 | 6 | L | = | = |  |
| Treatment | Physical damage when handling the hot air oven,hot plate,COD digester,muffle furnace and the autoclave in the lab. | Physical | Laboratory staff | 3 | Usage of PPE and follow the safety instructions (Eg.Heat adaptive gloves, Tone) | Visual Observations |  | 5 | 2 | 10 | M | = | = |  |
| Treatment | Physical harm from the fire by using the flammable chemicals. | Physical Chemical | Laboratory staff | 3 | 1.Store flammable chemicals properly. 2.Avoid open flames in the lab. 3.know the location and the operation of fire extinguishers 4.emergency exist. | Visual Inspection |  | 2 | 16 | 32 | H | = | = |  |
| Treatment | Physical harm from electrocution while using electrical lab equipment. | Physical | Laboratory staff | 3 | 1.Use equipment with grounded plugs. 2.Inspect cords and plug for damage | Visual Inspection |  | 2 | 16 | 32 | H | = | = |  |
| Treatment | Physical harm resulting from the broken laboratory glassware during the analysis. | Physical | Laboratory Staff | 3 | Keep away of broken glassware when doing the analysis. | Visual Inspection |  | 3 | 2 | 6 | L | = | = |  |
| Treatment | Carcinogenic impact from ultraviolet light exposure during the microbiological analysis. | Chemical | Laboratory Staff | 3 | Usage of PPE, Safety Cabinets and follow the safety instructions | Visual Inspections |  | 4 | 16 | 64 | VH | = | = |  |
| Treatment | Physical damage brought on due to the autoclave blasting during the analysis. | Physical | Laboratory Staff | 3 | Follow the safety Instructions | Visual Inspections |  | 2 | 16 | 32 | H | = | = |  |
| Treatment | Physical damage due to the slip of leg while climbing stairs of the WWTP | Physical | WWTP operation & maintenance personnel | 10 | Handrail & PPE | Visual observation |  | 2 | 8 | 16 | H | + | = | Suranga |
| Treatment | Physical damaged due to electrocution while operating the WWTP panel | Physical | Pump operators | 03 | - | - |  | 1 | 8 | 8 | M | + | = |  |
| Treatment | Physical damaged due to electrocution while repairing or PM in the WWTP panel | Physical | Electrical team | 03 | PPE | Visual observation |  | 2 | 16 | 32 | H | + | = |  |
| Treatment | Ingestion of wastewater due to falling into the sludge storage tank while opening the manhole covers for check the level of sludge | Biological | WWTP operation maintenance personnel and visitors | 50 | - | Visual observation |  | 2 | 8 | 16 | H | = | = |  |
| Treatment | Dermal contact with wastewater due to overflowing of the Sludge storage tank | Biological | WWTP Operation & Maintenance Personnel / Visitors | 50 | PPE | Visual observation |  | 3 | 2 | 6 | M | + | = |  |
| Treatment | Physical damaged due to blasting of a electrical panel | Physical | WWTP Operation & Maintenance Personnel / Visitors | 50 | - | Visual observation |  | 2 | 8 | 16 | H | + | = |  |
| Treatment | Physical damage due to Lightning shock while operating the Dehydrator electric panel. | Physical | WWTP Operation & Maintenance Personnel | 10 | PPE | Visual observation |  | 2 | 8 | 16 | H | + | - |  |
| Treatment | Physical damaged due to getting hand with the dehydrator machine while operating | Physical | WWTP Operation & Maintenance Personnel | 5 | - | Visual observation |  | 2 | 8 | 16 | H | = | = |  |
| Treatment | Physical injury due to the part of dehydrator break into pieces and hit on a personal while operating | Physical | WWTP Operation & Maintenance Personnel / Visitors | 50 | PPE | Visual observation |  | 2 | 4 | 8 | M | = | = |  |
| Treatment | Physical damaged by slipping of legs & fall down to the polymer tank while mixing polymer | Physical | Dehydrator Operation personnel | 2 | - | Visual observation |  | 2 | 8 | 16 | H | = | = |  |
| Treatment | Dermal contact with sludge due to Falling on the road while being transported | Biological | General Public | 25000 | - | Visual observation |  | 3 | 1 | 3 | L | + | - |  |
| End use or disposal | Ingestion of pathogens in surface water due to discharge of Activated sludge | Biological | General public | 5,000,000 | - | Visual observation |  | 3 | 2 | 6 | M | + | - | Indika |
| End use or disposal | Ingestion of pathogens in surface water due to discharge of partially treated effluent due to breakdown of aerators | Biological | General public | 5,000,000 | - | Visual observation |  | 3 |  |  |  |  |  | Indika |
| End use or disposal | Ingestion of pathogens in surface water due to discharge of partially treated effluent due to malfunction of chlorine dosing pump | Biological | general Public | 5,000,000 |  |  |  |  |  |  |  |  |  |  |

After discussions with your team, write in the following table which are the hazardous events that you will prioritize.

| Sanitation step | Hazardous event | Exposure Group | Number of persons at risk | Risk | Projection of changes in risks with climate change scenarios | Priority given |
| --- | --- | --- | --- | --- | --- | --- |

MODULE 4: DEVELOP AND IMPLEMENT AN INCREMENTAL IMPROVEMENT PLAN

STEP 4.1: Consider options to control identified risks

For each hazardous event prioritized, analyze the possible control measures using the following table:

| Step of the sanitation service chain: Description of the hazardous event: Exposure group: Improvement options |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Option of new or modified control measures for this hazardous event | What is the likely effectiveness of this control measure option? (High, medium, low) | What is the level of resources required? (Including financial, human resources, political support: high, medium, low) | To what extent will this control measure be effective under the most likely climate change scenarios? (Effective, ineffective, detrimental) | Comments/ discussion | Priority for improvement plan (Immediate, short term, medium term, long term) |

X

| Step of the sanitation service chain: Description of the hazardous event: Exposure group: Improvement options |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Option of new or modified control measures for this hazardous event | What is the likely effectiveness of this control measure option? (High, medium, low) | What is the level of resources required? (Including financial, human resources, political support: high, medium, low) | To what extent will this control measure be effective under the most likely climate change scenarios? (Effective, ineffective, detrimental) | Comments/ discussion | Priority for improvement plan (Immediate, short term, medium term, long term) |

X

| Step of the sanitation service chain: Description of the hazardous event: Exposure group: Improvement options |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Option of new or modified control measures for this hazardous event | What is the likely effectiveness of this control measure option? (High, medium, low) | What is the level of resources required? (Including financial, human resources, political support: high, medium, low) | To what extent will this control measure be effective under the most likely climate change scenarios? (Effective, ineffective, detrimental) | Comments/ discussion | Priority for improvement plan (Immediate, short term, medium term, long term) |

STEP 4.2: Develop an incremental improvement plan

Use the following Gantt Chart to plan the implementation of your improvement measures.

| Improvement measure | Cost | Source of funds | Lead organization | Year 1 |  |  |  |  |  |  |  |  |  |  |  | Year 2 |  |  |  | Year 3 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8 |
| Improvement measures to control prioritized hazardous event 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Improvement measures to control prioritized hazardous event 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Improvement measures to control prioritized hazardous event 3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

MODULE 5: Monitor control measures and verify performance

STEP 5.1: Define and implement operational monitoring

For each prioritized hazardous event and their improvement measures, choose 1 improvement measure that should have an operational monitoring plan.

| Prioritized hazardous event | Sanitation step | Choose one control measure that will have a detailed operational monitoring plan |
| --- | --- | --- |

Using the following tables, prepare the operational monitoring plan for the chosen control measures:

| Operational monitoring plan |  |  |  |  |
| --- | --- | --- | --- | --- |
| Operational monitoring plan for: |  |  |  |  |
| Operational limits | Operational monitoring of the control measure: Control measure: |  | Corrective action when the operational limit is exceeded |  |
|  | What is monitored? |  | What action is to be taken? |  |
|  | How is it monitored? |  |  |  |
|  | Where is it monitored? |  | Who takes the action? |  |
|  | Who monitors it? |  | When is it taken? |  |
|  | When is it monitored? |  | Who needs to be informed of the action? |  |

X

| Operational monitoring plan |  |  |  |  |
| --- | --- | --- | --- | --- |
| Operational monitoring plan for: |  |  |  |  |
| Operational limits | Operational monitoring of the control measure: Control measure: |  | Corrective action when the operational limit is exceeded |  |
|  | What is monitored? |  | What action is to be taken? |  |
|  | How is it monitored? |  |  |  |
|  | Where is it monitored? |  | Who takes the action? |  |
|  | Who monitors it? |  | When is it taken? |  |
|  | When is it monitored? |  | Who needs to be informed of the action? |  |

x

| Operational monitoring plan |  |  |  |  |
| --- | --- | --- | --- | --- |
| Operational monitoring plan for: |  |  |  |  |
| Operational limits | Operational monitoring of the control measure: Control measure: |  | Corrective action when the operational limit is exceeded |  |
|  | What is monitored? |  | What action is to be taken? |  |
|  | How is it monitored? |  |  |  |
|  | Where is it monitored? |  | Who takes the action? |  |
|  | Who monitors it? |  | When is it taken? |  |
|  | When is it monitored? |  | Who needs to be informed of the action? |  |

x

STEP 5.2: Verify system performance

For each prioritized hazardous event and their improvement, identify the verification plan.

| What is the control measure? | What is the objective of implementing this control measure? | How would you measure it? | Verification |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | What indicator will you use? | What is the maximum value you will accept? | When are you going to measure it? | Who will measure it? | How will it be measured? |

MODULE 6: DEVELOP SUPPORTING PROGRAMMES AND REVIEW PLANS

STEP 6.1: Identify and implement supporting programs

Write in the box below two supporting programs that should be implemented in the framework of Sanitation Safety planning.

|  | Supporting program 1 | Supporting program 2 |
| --- | --- | --- |
| Title of the program |  |  |
| Objective of the program |  |  |
| Description of the program |  |  |
| Key partners to implement the program |  |  |